## BatInverter data
Data label / Protocol | MEGAREVO PCS | SCU GRES | ECpvX Cluster | Sinexcel PWS2 | Atess PCS | Moura BESS | Sungrow ST129CP_50HV | Sinexcel PWS1 | Sinexcel PWG2 | PowerCombo 20C1H1000K | NR PCS-9765 | Huawei Smartlogger | PowerCombo 20C1H1000K | SCU BRES | MEGAREVO MPS | KEHAU BCS Series | Alpha ESS PCS | Growatt WIT | Poweroad GSSTES | Deye Hybrid
Serial number | % | % | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
Model | % | % | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | %
Version | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | %
AC power | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC power L1 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | x | x
AC power L2 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | x | x
AC power L3 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | x | x
AC reactive power | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC reactive power L1 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | % | x
AC reactive power L2 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | % | x
AC reactive power L3 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | % | x
AC apparent power | x | x | x | x | x | x | x | x | x | x | % | % | % | x | x | x | x | % | x | x
AC apparent power L1 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | % | %
AC apparent power L2 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | % | %
AC apparent power L3 | % | x | x | x | % | % | % | x | x | x | % | % | % | x | % | % | x | % | % | %
Power factor | x | % | x | x | % | x | x | x | x | x | x | % | % | % | x | % | x | % | x | %
Power factor L1 | % | x | x | x | % | % | % | x | x | x | % | % | % | % | % | % | x | % | % | %
Power factor L2 | % | x | x | x | % | % | % | x | x | x | % | % | % | % | % | % | x | % | % | %
Power factor L3 | % | x | x | x | % | % | % | x | x | x | % | % | % | % | % | % | x | % | % | %
Total energy export | x | % | x | x | % | % | x | x | x | x | x | % | % | % | x | x | x | x | % | %
Total energy import | x | % | x | x | % | % | x | x | x | x | x | % | % | % | x | x | x | x | % | %
L1-neutral voltage | % | x | x | % | % | x | x | % | % | % | x | % | % | % | % | % | % | % | x | x
L2-neutral voltage | % | x | x | % | % | x | x | % | % | % | x | % | % | % | % | % | % | % | x | x
L3-neutral voltage | % | x | x | % | % | x | x | % | % | % | x | % | % | % | % | % | % | % | x | x
L1-L2 phase to phase voltage | x | x | x | x | x | % | % | x | x | x | x | % | % | % | x | % | x | x | % | %
L2-L3 phase to phase voltage | x | x | x | x | x | % | % | x | x | x | x | % | % | % | x | % | x | x | % | %
L3-L1 phase to phase voltage | x | x | x | x | x | % | % | x | x | x | x | % | % | % | x | % | x | x | % | %
L1 phase current | x | x | x | x | x | x | x | x | x | x | x | % | % | % | x | x | x | x | x | x
L2 phase current | x | x | x | x | x | x | x | x | x | x | x | % | % | % | x | x | x | x | x | x
L3 phase current | x | x | x | x | x | x | x | x | x | x | x | % | % | % | x | x | x | x | x | x
LN phase current | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
Frequency L1 | x | x | x | x | % | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x
Frequency L2 | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
Frequency L3 | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
Cabinet temperature | x | % | x | x | x | x | x | x | x | x | % | % | % | % | x | x | x | x | x | %
State | x | x | x | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | x | x
Event field 01 | x | % | x | % | % | % | x | x | x | x | % | x | % | x | x | x | x | x | x | x
Event field 02 | x | % | x | % | % | % | x | % | % | % | % | x | % | x | x | x | x | x | x | x
Event field 03 | x | % | x | % | % | % | x | % | % | % | % | x | % | x | x | x | % | x | x | x
Event field 04 | x | % | x | % | % | % | x | % | % | % | % | % | % | % | x | x | % | x | x | x
DC current 01 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | %
DC voltage 01 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | %
DC power 01 | x | x | x | x | % | % | x | x | x | x | x | x | x | % | x | x | x | x | x | %
DC current 02 | % | % | x | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | %
DC voltage 02 | % | % | x | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | %
DC power 02 | % | % | x | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | %
State of charge | x | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x
State of energy | x | % | x | % | % | % | x | % | % | % | % | % | % | % | x | % | % | % | % | %
State of health | x | x | x | x | x | x | x | % | % | x | % | % | x | x | x | x | x | x | % | x
Charging capacity | x | x | x | x | x | x | x | % | % | % | x | x | % | x | x | x | % | x | x | %
Discharging capacity | x | x | x | x | x | x | x | % | % | % | x | x | % | x | x | x | % | x | x | %
Minimum cell voltage | x | % | x | x | x | x | x | % | % | x | % | % | x | x | x | % | x | % | x | %
Maximum cell voltage | x | % | x | x | x | x | x | % | % | x | % | % | x | x | x | % | x | % | x | %
Minimum cell temperature | x | % | x | x | x | x | x | % | % | % | % | % | x | x | x | % | x | % | % | %
Maximum cell temperature | x | % | x | x | x | x | x | % | % | % | % | % | x | x | x | % | x | % | % | %
BMS state | x | % | x | x | x | % | % | % | % | % | % | % | % | x | x | x | x | x | x | %
Minimum cell voltage channel | % | % | % | % | % | x | % | % | % | % | % | % | x | x | % | % | x | % | % | %
Maximum cell voltage channel | % | % | % | % | % | x | % | % | % | % | % | % | x | x | % | % | x | % | % | %
Minimum cell temperature channel | % | % | % | % | % | x | % | % | % | % | % | % | x | x | % | % | x | % | % | %
Maximum cell temperature channel | % | % | % | % | % | x | % | % | % | % | % | % | x | x | % | % | x | % | % | %
Control | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Seperate BMS interface needed | % | % | % | (%) | % | % | % | x | x | % | % | % | % | % | % | % | % | % | % | %

## BatInverter info
GENERAL INFORMATION
Besides controlling the power and reactive power generation of the inverters, the ECpvx is also capable of reading various data from them as part of its Data Acqusization scheme. The data is presented on the ECweb as well as made availbale via Modbus. Some of the data are possible to push to cloud as well. A gross list of which data the ECpvx is able to read out is shown below along with indications of which data from the gross list are read from the various inverter protocols supported.
SPECIFIC INFORMATION
Sinexcel PWS2 protocol: BMS data can be taken from the PCS. It depends on the battery which is connected to the sinexcel PCS. Function code 0x06 must be used.
Sicon GRES protocol: Function code 0x06 must be used.
Moura BESS protocol: Function code 0x10 must be used.
Sungrow ST129CP_50HV protocol: Function code 0x10 must be used.
Sinexcel PWS1 and PWG2 protocol: Function code 0x10 must be used. Seperate BMS communication required.
PowerCombo 20C1H1000K protocol: Function code 0x06 must be used.
ECpvX Cluster protocol: Function code 0x10 must be used.
NR PCS-9765 protocol: Function code 0x06 must be used.
ATESS PCS protocol: Function code 0x10 must be used.
Huawei Smartlogger protocol: Function code 0x10 must be used. "Huawei Smartlogger, PV" protcol to be used for the PV protocol selection.
Megarevo MPS: The PCS modbus ID is 0x14. The PCS ID in the ECpvX must therefore be set to 20.
Kehua BCS Series protocol: Function code 0x10 must be used.
Alpha-ESS: Function Code 0x10 must be used. NO reactive power control available.
Poweroad GSSTES: Function code 0x10 must be used.
Deye Hybrid: Function code 0x10 must be used.

## BMS data
Data label / Protocol | Polyntech | Greentech Caprack | Kgooer BAMS | MICA CBMS | PAN BMS PLD09
Serial number | % | % | % | % | %
Model | % | % | % | % | %
Version | % | % | % | % | %
BMS state | x | x | x | % | x
State of charge [0.1%] | x | x | x | x | x
State of energy [0.1kWh] | x | x | x | x | %
State of health [0.1%] | x | x | x | % | x
Maximum charge voltage [0.1V] | x | % | % | % | %
Maximum charge current [0.1A] | x | x | x | % | %
Online charging capacity [0.1kW] | x | x | x | % | %
Maximum discharge voltage [0.1V] | x | % | % | % | %
Maximum discharge current [0.1A] | x | x | x | % | %
Online charging capacity [0.1kW] | x | x | x | % | %
Minimum cell voltage [mV] | x | x | x | x | x
Maximum cell voltage [mV] | x | x | x | x | x
Minimum cell voltage channel | x | x | x | x | x
Maximum cell voltage channel | x | x | x | x | x
Minimum cell temperature [0.1C] | x | x | x | x | x
Maximum cell temperature [0.1C] | x | x | x | x | x
Minimum cell temperature channel | x | x | x | x | x
Maximum cell temperature channel | x | x | x | x | x
Minimum module voltage [0.1V] | x | % | % | % | %
Maximum module voltage [0.1V] | x | % | % | % | %
Minimum module voltage channel | x | x | % | % | x
Maximum module voltage channel | x | x | % | % | x
Minimum module temperature [0.1C] | x | % | % | % | %
Maximum module temperature [0.1C] | x | % | % | % | %
Minimum module temperature channel | x | x | % | % | x
Maximum module temperature channel | x | x | % | % | x
Number of piles/stacks | x | x | x | % | %
Number of modules in each pile/stack | x | % | % | % | %
DC current input [0.1A] | x | x | x | x | x
DC voltage input [0.1V] | x | x | x | x | x
DC power input [0.1kW] | x | % | x | x | x
Event field 1 | x | x | % | x | %
Event field 2 | x | % | % | x | %
Event field 3 | x | % | % | x | %
Event field 4 | x | % | % | x | %
Temperature [0.1C] | x | % | % | % | %
Control | x | % | % | % | x

## BMS info
GENERAL INFORMATION
Besides controlling the power and reactive power generation of the inverters, the ECpvx is also capable of reading various data from the BMS directly. The data is presented on the ECweb as well as made availbale via Modbus. Some of the data are possible to push to cloud as well. A gross list of which data the ECpvx is able to read out is shown below along with indications of which data from the gross list are read from the various BMS protocols supported.
SPECIFIC INFORMATION
Polyntech protocol: Function code 0x10 must be used.

## HVAC data
Data label / Protocol | BlackShields ACP
Serial number | %
Model | %
Version | %
HVAC state | x
Return temperature [0.1C] | x
Return humidity [0.1%] | x
Internal fan speed [rpm] | x
External fan speed [rpm] | x
Internal fan ON/OFF status | x
External fan ON/OFF status | x
Cooling ON/OFF status | x
Heating ON/OFF status | x
Sensor fault | x
High voltage alarm | x
Temperature alarm | x
Pressure alarm | x
Compressor fault | x
Heater fault | x
Internal fan alarm | x
External fan alarm | x
Inside temperature [0.1C] | %
Outside temperature [0.1C] | %
Control | %

## HVAC info
GENERAL INFORMATION
The ECpvX can read data from an HVAC system. The data is presented on the ECweb as well as made availbale via Modbus. Some of the data are possible to push to cloud as well. A gross list of which data the ECpvx is able to read out is shown below along with indications of which data from the gross list are read from the various HVAC protocols supported.
SPECIFIC INFORMATION

## Inverter data
Data label / Protocol | SunSpec | SolarEdge | Delta Solvia | SUN2000-8-28KTL | Huawei Smartlogger | ABB TRIO 20/27.6 | SUN2000-V3.0 | Sungrow SG | SUN2000-V2.0 | Schneider ConextCL | SMA Solid Q 50 | SMA Solid Q 60 | Growatt | Sofar 1_40kW | Sofar 50_70kW | Growatt MAX | Ginlong Solis | Polycab | ABB TRIO 50_60 | KStar | Kehua SPI-B | SMA Webbox nn000TL-10 | Goodwe DT | Goodwe MT | AISWEI | Goodwe HT | INVT BG | Sungrow COM100E | CPS 14_36kW | CPS SCA 18_36kW | Sofar 80_136kW | WEG SIW750 | DEYE | SMA DATAMANAGER | INVT XG | Solax X3-MEGA and G2G3 Forth | Ingeteam 3Play | Afore PV
Serial number | x | x | x | % | % | x | x | x | % | x | x | x | % | x | x | % | x | x | x | % | x | % | x | x | x | x | x | % | x | x | x | % | x | % | x | x | % | %
Model | x | x | % | % | % | x | x | x | % | x | % | % | % | x | x | % | % | % | x | % | x | x | x | x | x | x | x | % | x | x | % | % | % | % | % | % | % | %
Version | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | %
AC power | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC reactive power | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | % | % | x | % | x | x | % | x | x | x | x | x | x | x | x | x
AC apparent power | x | x | x | % | % | % | % | x | % | x | % | % | % | % | % | % | x | x | % | x | x | x | % | % | x | % | % | % | x | % | x | x | x | % | % | x | x | x
Power factor | x | x | x | x | x | % | x | x | x | x | x | x | % | % | % | % | x | x | % | % | x | % | % | % | x | % | x | % | % | % | % | x | x | % | x | x | x | x
Total energy production | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | x | x | x | x | x | % | x | x | x | x
Daily energy production | % | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | x | x | x | x | x | % | x | x | x | x
Total operating time | % | % | x | x | % | % | % | x | x | x | x | x | x | x | x | x | % | % | % | % | % | % | x | x | x | x | % | % | % | x | % | % | % | % | x | % | x | %
Daily operating time | % | % | x | % | % | % | % | x | % | x | % | % | % | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
L1-neutral voltage | x | x | x | % | % | x | x | % | x | % | x | % | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | % | % | x | x | % | x | % | x | x | x | x
L2-neutral voltage | x | x | x | % | % | % | x | % | x | % | x | % | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | % | % | x | x | % | x | % | x | x | x | x
L3-neutral voltage | x | x | x | % | % | % | x | % | x | % | x | % | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | % | % | x | x | % | x | % | x | x | x | x
L1-L2 phase to phase voltage | x | x | % | x | % | x | x | x | x | x | % | x | % | % | % | x | x | x | % | x | % | % | % | % | x | x | % | % | x | % | % | x | x | % | x | x | % | %
L2-L3 phase to phase voltage | x | x | % | x | % | x | x | x | x | x | % | x | % | % | % | x | x | x | % | x | % | % | % | % | x | x | % | % | x | % | % | x | x | % | x | x | % | %
L3-L1 phase to phase voltage | x | x | % | x | % | x | x | x | x | x | % | x | % | % | % | x | x | x | % | x | % | % | % | % | x | x | % | % | x | % | % | x | x | % | x | x | % | %
L1 phase current | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | % | x | x | x | x
L2 phase current | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | % | x | x | x | x
L3 phase current | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | % | x | x | x | x
Frequency | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | % | x | x | x | x
Cabinet temperature | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | x | x | x | % | % | % | x | x | % | %
State | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | % | x | x | x | x | x | % | x | x | x | x
Event field 01 | x | % | % | % | x | x | x | x | % | x | x | x | x | x | x | % | % | % | % | x | % | % | x | x | x | % | % | % | x | x | % | % | x | % | x | % | x | x
Event field 02 | x | % | % | % | x | % | x | % | % | % | % | % | % | x | x | % | % | % | % | x | % | % | % | % | x | % | % | % | x | % | % | % | x | % | x | % | x | x
Event field 03 | % | % | % | % | x | % | x | % | % | % | % | % | % | x | x | % | % | % | % | x | % | % | % | % | % | % | % | % | x | % | % | % | x | % | x | % | x | x
Event field 04 | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | x | % | x | % | x | x
DC current 01 | x | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | % | x | x | % | x
DC voltage 01 | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | % | x | x | % | x
DC power 01 | x | x | x | % | % | x | % | % | x | % | % | % | x | x | x | x | % | % | % | x | % | x | % | % | % | % | % | % | % | x | x | % | % | % | % | % | % | x
DC current 02 | x | % | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | x | x | x | x | x | % | x | x | % | x
DC voltage 02 | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | x | x | x | x | x | % | x | x | % | x
DC power 02 | x | % | x | % | % | x | % | % | x | % | % | % | x | x | x | x | % | % | % | x | % | % | % | % | % | % | % | % | % | x | x | % | % | % | % | % | % | x
DC current 03 | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | x | x | % | x | x | % | % | x | % | x | x | % | % | x | x | % | x | % | x | x | % | x
DC voltage 03 | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | x | x | % | x | x | % | % | x | % | x | x | % | % | x | x | % | x | % | x | x | % | x
DC power 03 | x | % | x | % | % | % | % | % | x | % | x | x | % | % | x | x | % | % | % | x | % | % | % | % | % | % | % | % | % | x | x | % | % | % | % | % | % | x
DC current 04 | x | % | x | x | % | % | x | x | x | x | x | x | % | % | % | x | x | x | % | % | x | % | % | x | % | x | x | % | % | x | x | % | x | % | x | x | % | x
DC voltage 04 | x | % | x | x | % | % | x | x | x | x | x | x | % | % | % | x | x | x | % | % | x | % | % | x | % | x | x | % | % | x | x | % | x | % | x | x | % | x
DC power 04 | x | % | x | % | % | % | % | % | x | % | x | x | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | x | x | % | % | % | % | % | % | x
Control | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x

## Inverter info
GENERAL INFORMATION
Besides controlling the power and reactive power generation of the inverters, the ECpv is also capable of reading various data from them as part of its Data Acqusization scheme. The data is presented on the ECweb as well as made availbale via Modbus. Some of the data are possible to push to cloud as well. A gross list of which data the ECpv is able to read out is shown below along with indications of which data from the gross list are read from the various inverter protocols supported. Note that for SunSpec protocol the available data furthermore depends on the individual vendors implementation of SunSpec.
SPECIFIC INFORMATION
SolarEdge protocol: Control function 0x10 must be used. Ecpv make use of the "Enhanced Power Control Dynamic Commands". Initial setup of inverters required in accordance with SolarEdge documentation
Delta Solvia protocol: Control function 0x06 must be used. Function code 0x10 not supported by Delta/Solvia.
Huawei SmartLogger protocol: Control function 0x10 must be used. Function code 0x06 can't be used as references send as 32 bit values. RTU ControlID must be set to "0". Meteorological data can be read via Smartlogger. SensorID1 must in this case be set to ID of the weatherstation connected to the SmartLogger.
ABB Trio protocol: Control function 0x10 must be used. Trio actually support both 0x06 and 0x10 but only 0x10 support added on ECpv side for Trio.
Sungrow SG protocol: Control function 0x10 must be used. Sungrow SG actually support both 0x06 and 0x10 but only 0x10 support added on ECpv side for Sungrow SG.
Huawei SUN2000_8_28KTL and SUN2000_V2.0: Some parameters are only written to inverters during initialization. These parameters are for configuring the inverters to listen to reference commands comming via commnication. The parameters can't be written to continuously. They are therefore written to only once as the protocol is selected in the ECpv. The invterers will remember the parameters afterwards also after being powered down/up. Therefore make sure that all inverters are receiving on communication line when the protocol is enabled in the ECpv.
SMA SolidQ: Control function 0x10 must be used. For broadcast frames SolidQ supports only 0x10.
Growatt & Growatt MAX: Note that reactive power is not read as part of data acquisition. If ECpv is to do reactive power control that rely on a reactive power reading a power meter need to be installed.
Sofar: Note that reactive power is not contolled. Function code 0x06 must be used. Broadcast ID must be set to 136.
Ginlog Solis: Note that Broadcast commands are not supported.
Polycab: Note that Broadcast commands are not supported.
KStar: Control function 0x06 must be used. Function code 0x10 not supported by KStar.
Kehua SPI-B: All inverters must be of same rating.
SMA Webbow STP nn000TL-10 protocol: Control function 0x10 must be used.
Goodwe DT: Note that reactive power is not read as part of data acquisition. If ECpv is to do reactive power control that rely on a reactive power reading a power meter need to be installed.
Goodwe MT: Note that reactive power is not read as part of data acquisition. Furthermore active power is combined of two seperate word readings. If ECpv is to do reactive power control that rely on a reactive power reading a power meter need to be installed. Power meter recommended in any case due to the active power reading potentially being off when power being produced ocsilliates aroung 65.635kW
Sungrow COM100E: Control function 0x10 must be used. Acquisition from the inverters is not possible - only control plus reading of the total PV production. Modbus ID: 247
CPS 14_36kW: Function code 0x06 must be used. Note that reactive power is not read as part of data acquisition. If ECpv is to do reactive power control that rely on a reactive power reading a power meter need to be installed.
CPS SCA 18_36kW: Function code 0x06 must be used.
Sofar 80-163kW: Function code 0x10 must be used.
WEG SIW750: Function code 0x10 must be used.
DEYE: Function code 0x10 must be used.
Ingeteam 3Play: Function code 0x10 must be used
Afore PV: Function code 0x10 must be used

## Meter data
Data label / Protocol | Pilot SPM32 | Pilot SPM33 | Acuvim-L | Acuvim EV300 | Schneider iEM3000 | Schneider PM51XX | Schneider PM53XX | Schneider PM55XX | Deif ml2 | Deif CGC400 | Cummins PC2.x | Cummins PC3.x | Cat EMCP4 | DSE GenComm | Deif ml2 Mains | Entes EPM07S | Janitza UMG96RM | Comap AMF20/25 | Comap InteliLite9 | Comap InteliGen | Comap InteliSys | Schneider PM1200/EM64XX | DEIF MIC-2 | Comap InteliComact | WW EasyGen2000 | WW EasyGen3000 | Klemsan Ercas | Klemsan Krea | Klemsan Powys | Phoenix EEM-EM3XX | Pheonix EMPro | Eastron SDM630 | Schneider PM2XXX | SmartGen HGM400 | Socomec Diris A40 | Chint DTSU/DSSU 666 | Lovato SGK60 | Secure Elite 440 | ABB M4M 30 | Secure Elite 300 | Aldogue UPM209 | PILOT PMAC770 | SmartGen HGM 7X00_9X00 | Circutor CVM C4 | Sices GC310/350/500 | Sices MC100 | Huawei Smartlogger | Elgris Smartmeter | CG EM/ET 300 series | WW EasyGen3000XT | LETTEL MCT4 | SIEMENS PCS3120 | AcuvimII | SGC120/121 | DFUN DFPM93 | LETTEL MCX-34V | Datakom D300_500_700 | Comap InteliGen_4_200 | Comap InteliMains_210 | Acrel ADL3000-E | Selec MFM384 | SMA DataManager | Sices MC200_400 | Cummins MCM3320 | Siemens 7kt0310 | IME Nemo96EA | Comap InteliGen 1000
AC power phase L1 | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x
AC power phase L2 | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x
AC power phase L3 | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x
AC power total | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC reactive power phase L1 | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x
AC reactive power phase L2 | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x
AC reactive power phase L3 | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x
AC reactive power total | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC apparent power phase L1 | % | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x
AC apparent power phase L2 | % | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x
AC apparent power phase L3 | % | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x
AC apparent power total | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x
AC power factor phase L1 | x | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | % | x | x | x
AC power factor phase L2 | x | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | % | x | x | x
AC power factor phase L3 | x | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | % | x | x | x
AC power factor total | x | x | x | x | % | % | % | % | x | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC current phase L1 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | % | x | x | x | x | x
AC current phase L2 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | % | x | x | x | x | x
AC current phase L3 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | % | x | x | x | x | x
AC current neutral conducter | x | x | x | x | x | x | x | x | % | % | x | x | % | % | % | x | x | % | % | % | % | % | x | % | % | % | x | x | x | x | x | % | x | % | x | % | % | x | x | x | x | x | % | % | x | x | % | % | % | % | % | % | x | % | % | % | x | % | % | % | % | % | x | % | % | x | %
AC voltage L1-neutral | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x
AC voltage L2-neutral | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x
AC voltage L3-neutral | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x
AC voltage L1-L2 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x
AC voltage L2-L3 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x
AC voltage L3-L1 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x
AC frequency phase L1 | x | x | x | x | % | % | % | % | x | x | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | % | % | x | % | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x
AC frequency phase L2 | % | % | % | % | % | % | % | % | x | x | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | %
AC frequency phase L3 | % | % | % | % | % | % | % | % | x | x | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | %
AC energy total | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | x | % | % | % | % | x | x | x | % | % | % | x | % | % | % | x | % | %
AC energy imported total | x | x | x | % | x | % | % | % | % | % | % | % | % | x | % | % | x | % | % | % | % | % | x | % | % | % | % | % | % | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | % | % | % | % | % | % | x | % | x | x | %
AC energy exported total | x | x | x | % | x | % | % | % | % | % | % | % | % | x | % | % | x | % | % | % | % | % | x | % | % | % | % | % | % | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | % | % | % | % | % | % | x | % | x | x | %
AC reactive energy total | x | x | % | % | % | % | % | % | % | % | % | % | % | x | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | x | % | % | % | % | x | x | % | % | % | % | x | % | % | % | x | % | %
AC reactive inductive energy total | x | x | x | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | x | % | % | % | % | % | x | % | x | x | %
AC reactive capacitive energy total | x | x | x | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | x | % | % | % | % | % | x | % | x | x | %
Digital input | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | % | x | x | x | x | % | % | % | x | x | % | % | % | % | % | % | % | % | % | % | x | % | x | % | % | % | % | % | x | % | % | % | x | % | % | % | x | x | % | % | % | % | % | % | % | %
Digital output | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | x | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
DG Management start/stop command | Relay | Relay | % | % | % | % | % | % | communication | communication | % | % | % | % | % | % | Relay | % | % | % | % | % | Relay | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | Relay | % | Relay | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %

## Meters info
GENERAL INFORMATION
The ECpv will be reading various data from genset controllers and/or power meters. The data is presented on the ECweb as well as made availbale via Modbus. Some of the data are possible to push to cloud as well. A gross list of which data the ECpv is able to read out is shown below along with indications of which data from the gross list are read from the protocols supported. Digital input can be used for breaker closed feedback. In case it be from a power meter digital input #1 is used. In case it be from a genset controller the breaker on status can in most cases be read directly from the input used by the genset controller itself. If not the breaker on detection type need to be set to "Genset Power". Digital output can be used for signalling in the event of an alarm being prooked in the ECpv.
SPECIFIC INFORMATION
JanitzaUMG96 protocol: Outouts need to be configured to Modbus control. Initial setup of outouts required in accordance with Janitza documentation
DEIF ml2 & DEIF CGC400 protocol: When to use DG management the genset controllers must be put in automatic mode. The command given by Ecpv is the "Auto start/stop" command. Consult DEIF modbus documentation to learn which of the ml2 controllers that support this command.
Schneider: Float byte order in the metres must set to Big-Endian.

## Sensor data
Data label / Protocol | SunSpec | SI-RS485 | TM-RS485 | AMB-RS485 | Huawei Smartlogger | SevenSolar | Sungrow PC-4 | SMA Webbox | Rainwise Pvmet | LiteMeter Pro | Hukseflux SR05 | SunMeter Pro | EnvMeter PRO | KippZonen SMP | BDSensor DCL531 | WindMeter | Sunmeter PRO wind | Rica RK200 | Rica RK220 | SAH XY-MD02 | Lufft WS200 | LogicsPowerAMR PYRA 300V
POA | x | x | % | % | % | x | x | x | x | x | x | x | % | x | % | % | x | x | % | % | x | x
GHI | x | x | % | % | x | x | x | x | x | x | x | x | % | x | % | % | x | x | % | % | x | x
BOM | x | x | x | % | x | % | % | x | x | % | % | x | % | % | % | % | x | % | x | % | x | x
Amb. Temperature | x | x | % | x | x | x | x | x | x | % | % | x | x | % | % | % | x | % | x | x | x | x
Wind speed | x | x | % | % | x | x | x | x | % | % | % | % | % | % | % | x | x | % | % | % | x | %
Relative humidity | x | % | % | % | % | x | x | x | % | % | % | % | x | % | % | % | % | % | % | x | x | %
Barometrical pressure | x | % | % | % | % | % | x | x | % | % | % | % | % | % | % | % | % | % | % | % | x | %
Wind direction | x | % | % | % | x | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | x | %
Rain fall | x | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | x | %
Fuel pressure | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | %

## Sensor info
GENERAL INFORMATION
The ECpv is capable of reading various meteorological data. The data can be read from seperate sensors or as part of the inverter communication. The data is presented on the ECweb as well as made availbale via Modbus. Some of the data are possible to push to cloud as well. Note that when reading via Inverter SunSpec protocol the available data furthermore depends on the individual vendors implementation of SunSpec.
SPECIFIC INFORMATION
Huawei Smartlogger: Is via the inverter communication
SunSpec: Is via the inverter communication
Sungrow PC-4 MetMast: Is via the inverter communication
SMA Webbox: Is via the inverter communication (either from SMA Sensorbox or SMA Meteo station connected to the Webbox)
Rainwise Pvmet: Only one irradiance input supported by the weather station which can then be mapped to either POA or GHI in the ECpv
LiteMeter Pro: Only one irradiance input supported by the weather station which can then be mapped to either POA or GHI in the Ecpv. The internal cell temperature is taken for the BOM measurement.
Hukseflux SR05: Only one irradiance input supported by the weather station which can then be mapped to either POA or GHI in the ECpv
SunMeter Pro: Only one irradiance input supported by the weather station which can then be mapped to either POA or GHI in the Ecpv. The internal cell temperature is taken for the BOM measurement. If a PT100 sensor is connected it will be used as Ambient temp.
KippZonen SMP: Only one irradiance input supported which can then be mapped to either POA or GHI in the Ecpv.
BDSensor DCL531 (551, 571): The unit selector in the sensor must be set to [Bar].
WindMeter: Unit must be set to [m/s] as it is per default.
Rica RK200: Only one irradiance input supported which can then be mapped to either POA or GHI in the Ecpv.
Rica RK220: Only one temperature input supported which can then be mapped to either BOM or Ambient tmeperature in the Ecpv.

## IO data
Data label / Protocol | EX0008DD | EX1600DD | EX16008DD | Huawei Smartlogger | DEIF ML2 BTB | DSE8680 | EX04AIO | EX04AIS | Woodward LS-5
Digital input | 0 | 16 | 16 | 8 | 1 | 1 | 0 | 0 | 8
Digital output | 8 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Analogue Input | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0
Analogue output | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0

## IO info
GENERAL INFORMATION
The ECpv is capable of interfacing to IO modules. Up to 4 IO modules can be connected. The data is presented on the ECweb as well as made available via Modbus.
SPECIFIC INFORMATION
DEIF ML2 BTB: The input read is the position of the busbar coupler
DSE8680: The input read is the position of the busbar coupler
EX04AIO/EX04AIS: The input and output can be selected as 0-10V or 0-20mA.
Woodward LS-5: The inputs read are the 8 discrete inputs on the device

## ECsync data
Data label / Protocol | AGC150 Mains
Serial number | %
Model | %
Version | x
Grid side AC voltage L1-L2 | x
Grid side AC voltage L2-L3 | x
Grid side AC voltage L3-L1 | x
Grid side AC voltage L1-neutral | x
Grid side AC voltage L2-neutral | x
Grid side AC voltage L3-neutral | x
Grid side AC frequency phase L1 | x
Grid side AC frequency phase L2 | x
Grid side AC frequency phase L3 | x
Grid side AC voltage L1-L2 angle | x
Grid side AC voltage L2-L3 angle | x
Grid side AC voltage L3-L1 angle | x
AC current phase L1 | x
AC current phase L2 | x
AC current phase L3 | x
AC power phase L1 | x
AC power phase L2 | x
AC power phase L3 | x
AC power total | x
AC reactive power phase L1 | x
AC reactive power phase L2 | x
AC reactive power phase L3 | x
AC reactive power total | x
AC apparent power phase L1 | x
AC apparent power phase L2 | x
AC apparent power phase L3 | x
AC apparent power total | x
Busbar side AC voltage L1-L2 | x
Busbar side AC voltage L2-L3 | x
Busbar side AC voltage L3-L1 | x
Busbar side AC voltage L1-neutral | x
Busbar side AC voltage L2-neutral | x
Busbar side AC voltage L3-neutral | x
Busbar side AC frequency phase L1 | x
Busbar side AC frequency phase L2 | x
Busbar side AC frequency phase L3 | x
Busbar side AC voltage L1-L2 angle | x
Busbar side AC voltage L2-L3 angle | x
Busbar side AC voltage L3-L1 angle | x
Busbar-grid AC voltage L1-L1 angle | x
Busbar-grid AC voltage L2-L2 angle | x
Busbar-grid AC voltage L3-L3 angle | x
Digital input | x
Digital output | x

## ECsync info
GENERAL INFORMATION
The ECpv is capable of interfacing to the ECsync cabinet. 1 Ecsync cabinet can be connected. The data is presented on the ECweb as well as made available via Modbus.
SPECIFIC INFORMATION