## EMS_data
Data label / Protocol | Ecpvx
PV Active Power Generating Capacity | x
Genset Active Power Generating Capacity | x
Mains Active Power Generating Capacity | x
Battery Active Power Generating Capacity | x
PV Total Active Power | x
Genset Total Active Power | x
Mains Total Active Power | x
Battery Total Active Power | x
PV Total Reactive Power | x
Genset Total Reactive Power | x
Mains Total Reactive Power | x
Battery Total Reactive Power | x
SOC | x
SOH | x
SOE | x
ODC | x
OCC | x
MAC Address | x
Stop All Charging SOC Threshold | x
Stop All Discharging SOC Threshold | x
Genset Charge Start SOC Threshold | x
Genset Charge Stop SOC Threshold | x
Mains Charge Start SOC Threshold | x
Mains Charge Stop SOC Threshold | x
PV Charge Start SOC Threshold | x
PV Chrage Stop SOC Threshold | x
Genset SOC Threshold Enable | x
Mains SOC Threshold Enable | x
PV SOC Threshold Enable | x
Mains P Control Mode | x
Mains Battery P Control Mode | x
Mains Q Control Mode | x
Mains Battery Q Control Mode | x

## EMS_info
GENERAL INFORMATION
Ecev must interface with an EMS that supplies information about the battery's SOC and the power capacities of the grid connection and battery at the minimum. Multiple functionalities of the ECev only work if certain data acquisitions from the EMS are present. Uploading data to ECcloud is only possible if ECpvX is used as EMS.
SPECIFIC INFORMATION

## EV_data
Data label / Protocol | SCUPOWER | BENYI
Station
Power | x | %
Reactive Power | % | %
Apparent Power | % | %
Power Factor | % | %
Voltage L1-LN | x | %
Voltage L2-LN | x | %
Voltage L3-LN | x | %
Voltage L1-L2 | % | %
Voltage L2-L3 | % | %
Voltage L3-L1 | % | %
Current L1 | % | %
Current L2 | % | %
Current L3 | % | %
Frequency | % | %
DCU | % | %
DCA | % | %
DCP | % | %
State | x | %
Event field 1 | % | x
Event field 2 | % | x
Event field 3 | % | %
Event Field 4 | % | %
Charging Guns
State | x | x
Power | % | x
CarID | x | x

## EV_info
GENERAL INFORMATION
SPECIFIC INFORMATION
SCUPOWER: Function code 0x10 must be used.
BENYI: Function code 0x06 must be used.

## IO data
Data label / Protocol | EX0008DD | EX1600DD | EX16008DD | Huawei Smartlogger | DEIF ML2 BTB | DSE8680 | EX04AIO | EX04AIS | Woodward LS-5
Digital input | 0 | 16 | 16 | 8 | 1 | 1 | 0 | 0 | 8
Digital output | 8 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Analogue Input | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0
Analogue output | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0

## IO info
GENERAL INFORMATION
The ECpv is capable of interfacing to IO modules. Up to 4 IO modules can be connected. The data is presented on the ECweb as well as made available via Modbus.
SPECIFIC INFORMATION
DEIF ML2 BTB: The input read is the position of the busbar coupler
DSE8680: The input read is the position of the busbar coupler
EX04AIO/EX04AIS: The input and output can be selected as 0-10V or 0-20mA.
Woodward LS-5: The inputs read are the 8 discrete inputs on the device