## Input Register 0x04
EV Charger number 1 to 32 The addressses of genset meter number x is found by: AddressMeter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
0..15 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
16..31 | MODEL | Char, 32 byte Ascii characters | EV Charger model | Not defined
32..39 | VERSION | Char, 16 byte Ascii characters | Version | Not defined
40..49 | RESERVED | Not defined | Reserved for later use | Not defined
50..51 | POWER | 32 signed int (byte order: ABCD) | Active Power [W] | 0x80000000
52..53 | REPOWER | 32 signed int (byte order: ABCD) | Reactive Power [W] | 0x80000000
54..55 | APPOWER | 32 signed int (byte order: ABCD) | Apparent Power [W] | 0x80000000
56 | PF | 16 signed int | Power Factor | 0x8000
57 | VOLTAGE_L1N | 16 unsigned int | Line 1 to neutral voltage on the AC bus [0.1 V] | 0xFFFF
58 | VOLTAGE_L2N | 16 unsigned int | Line 2 to neutral voltage on the AC bus [0.1 V] | 0xFFFF
59 | VOLTAGE_L3N | 16 unsigned int | Line 3 to neutral voltage on the AC bus [0.1 V] | 0xFFFF
60 | VOLTAGE_L1L2 | 16 unsigned int | Line 1 to Line 2 voltage on the AC bus [0.1 V] | 0xFFFF
61 | VOLTAGE_L2L3 | 16 unsigned int | Line 2 to Line 3 voltage on the AC bus [0.1 V] | 0xFFFF
62 | VOLTAGE_L3L1 | 16 unsigned int | Line 3 to Line 1 voltage on the AC bus [0.1 V] | 0xFFFF
63 | CURRENT_L1 | 16 signed int | Line 1 Current on the AC bus [0.1 A] | 0x8000
64 | CURRENT_L2 | 16 signed int | Line 2 Current on the AC bus [0.1 A] | 0x8000
65 | CURRENT_L3 | 16 signed int | Line 3 Current on the AC bus [0.1 A] | 0x8000
66 | FREQ | 16 unsigned int | AC bus frequency [0.01 Hz] | 0xFFFF
67 | DCU | 16 unsigned int | DC bus voltage [0.1 V] | 0xFFFF
68 | DCA | 16 signed int | DC bus current [0.1 A] | 0x8000
69 | DCP | 16 signed int | DC bus power [0.1 kW] | 0x8000
70 | STATE | 16 unsigned int | EV charging station working state | 0xFFFF
71..72 | EVT1 | 32 unsigned int (byte order: ABCD) | Event field 01 | 0xFFFFFFFF
73..74 | EVT2 | 32 unsigned int (byte order: ABCD) | Event field 02 | 0xFFFFFFFF
75..76 | EVT3 | 32 unsigned int (byte order: ABCD) | Event field 03 | 0xFFFFFFFF
77..78 | EVT4 | 32 unsigned int (byte order: ABCD) | Event field 04 | 0xFFFFFFFF
79 | STATION_NBROF_GUNS | 16 unsigned int | Number of charging guns on the station | 0xFFFF
80..99 | RESERVED | Not defined | Reserved for later use | Not defined
100 | GUN1_STATE | 16 unsigned int | Gun #1 status | 0xFFFF
101..102 | GUN1_POWER | 32 signed int (byte order: ABCD) | Gun #1 active power [W] | 0xFFFFFFFF
103..110 | GUN1_CARID | Char, 16 byte Ascii characters | EV CAR ID on Gun #1 | Not defined
111..119 | RESERVED | Not defined | Reserved for later use | Not defined
120 | GUN2_STATE | 16 unsigned int | Gun #2 status | 0xFFFF
121..122 | GUN2_POWER | 32 signed int (byte order: ABCD) | Gun #2 active power [W] | 0xFFFFFFFF
123..130 | GUN2_EVCCID | Char, 16 byte Ascii characters | EV Communication Controller ID of Car on Gun #2 | Not defined
131..139 | RESERVED | Not defined | Reserved for later use | Not defined
140 | GUN3_STATE | 16 unsigned int | Gun #3 status | 0xFFFF
141..142 | GUN3_POWER | 32 signed int (byte order: ABCD) | Gun #3 active power [W] | 0xFFFFFFFF
143..150 | GUN3_EVCCID | Char, 16 byte Ascii characters | EV Communication Controller ID of Car on Gun #3 | Not defined
151..159 | RESERVED | Not defined | Reserved for later use | Not defined
160 | GUN4_STATE | 16 unsigned int | Gun #4 status | 0xFFFF
161..162 | GUN4_POWER | 32 signed int (byte order: ABCD) | Gun #4 active power [W] | 0xFFFFFFFF
163..170 | GUN4_EVCCID | Char, 16 byte Ascii characters | EV Communication Controller ID of Car on Gun #4 | Not defined
171..198 | RESERVED | Not defined | Reserved for later use | Not defined
199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
IO module number 1 to 4 The addressses of module number x is found by: AddressModule_x = (x-1) * 50 + Address
Address | DataLabel | DataType | Description | Not available value
20500 | INPUT_1_16 | 16 unsigned int | bitwise | Not defined
20501 | OUTPUT_1_16 | 16 unsigned int | bitwise | Not defined
20502..20503 | AIO_INPUT_01 | FLOAT (byte order: ABCD) | Analogue input 01 | Not defined
20504..20505 | AIO_INPUT_02 | FLOAT (byte order: ABCD) | Analogue input 02 | Not defined
20506..20507 | AIO_INPUT_03 | FLOAT (byte order: ABCD) | Analogue input 03 | Not defined
20508-20509 | AIO_INPUT_04 | FLOAT (byte order: ABCD) | Analogue input 04 | Not defined
20510..20511 | AIO_INPUT_05 | FLOAT (byte order: ABCD) | Analogue input 05 | Not defined
20512..20513 | AIO_INPUT_06 | FLOAT (byte order: ABCD) | Analogue input 06 | Not defined
20514..20515 | AIO_INPUT_07 | FLOAT (byte order: ABCD) | Analogue input 07 | Not defined
20516..20517 | AIO_INPUT_08 | FLOAT (byte order: ABCD) | Analogue input 08 | Not defined
20518..20519 | AIO_OUTPUT_01 | FLOAT (byte order: ABCD) | Analogue output 01 | Not defined
20520..20521 | AIO_OUTPUT_02 | FLOAT (byte order: ABCD) | Analogue output 02 | Not defined
20522..20523 | AIO_OUTPUT_03 | FLOAT (byte order: ABCD) | Analogue output 03 | Not defined
20524..20525 | AIO_OUTPUT_04 | FLOAT (byte order: ABCD) | Analogue output 04 | Not defined
20526..20527 | AIO_OUTPUT_05 | FLOAT (byte order: ABCD) | Analogue output 05 | Not defined
20528..20529 | AIO_OUTPUT_06 | FLOAT (byte order: ABCD) | Analogue output 06 | Not defined
20530..20531 | AIO_OUTPUT_07 | FLOAT (byte order: ABCD) | Analogue output 07 | Not defined
20532..20533 | AIO_OUTPUT_08 | FLOAT (byte order: ABCD) | Analogue output 08 | Not defined
20534 | CH_CONF_01 | 16 unsigned int | Channel confirguration 01 | Not defined
20535 | CH_CONF_02 | 16 unsigned int | Channel confirguration 02 | Not defined
20536 | CH_CONF_03 | 16 unsigned int | Channel confirguration 03 | Not defined
20537 | CH_CONF_04 | 16 unsigned int | Channel confirguration 04 | Not defined
20538 | CH_CONF_05 | 16 unsigned int | Channel confirguration 05 | Not defined
20539 | CH_CONF_06 | 16 unsigned int | Channel confirguration 06 | Not defined
20540 | CH_CONF_07 | 16 unsigned int | Channel confirguration 07 | Not defined
20541 | CH_CONF_08 | 16 unsigned int | Channel confirguration 08 | Not defined
20542 | CH_STATUS | 16 unsigned int | Channel status | Not defined
20543 | MOD_TEMP | 16 unsigned int | Module temperature [0.1C] | Not defined
20544..20548 | RESERVED | Not defined | Reserved for later use | Not defined
20549 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
EMS ACQUISITION
21000..21001 | PV_P_CAPACITY | FLOAT (byte order: ABCD) | PV active power capacity [kW] | Not defined
21002..21003 | DG_P_CAPACITY | FLOAT (byte order: ABCD) | DG active power capacity [kW] | Not defined
21004..21005 | MAINS_P_CAPACITY | FLOAT (byte order: ABCD) | Mains active power capacity [kW] | Not defined
21006..21007 | BAT_P_CAPACITY | FLOAT (byte order: ABCD) | Battery active power capacity [kW] | Not defined
21008..21009 | PV_P_TOTAL | FLOAT (byte order: ABCD) | PV Total active power production [kW] | Not defined
21010..21011 | DG_P_TOTAL | FLOAT (byte order: ABCD) | DG Total active power production [kW] | Not defined
21012..21013 | MAINS_P_TOTAL | FLOAT (byte order: ABCD) | Mains Total active power production [kW] | Not defined
21014..21015 | BAT_P_TOTAL | FLOAT (byte order: ABCD) | Battery Total active power production [kW] | Not defined
21016..21017 | PV_Q_TOTAL | FLOAT (byte order: ABCD) | PV Total reactive power production [kVar] | Not defined
21018..21019 | DG_Q_TOTAL | FLOAT (byte order: ABCD) | DG Total reactive power production [kVar] | Not defined
21020..21021 | MAINS_Q_TOTAL | FLOAT (byte order: ABCD) | Mains Total reactive power production [kVar] | Not defined
21022..21023 | BAT_Q_TOTAL | FLOAT (byte order: ABCD) | Battery Total reactive power production [kVar] | Not defined
21024..21025 | BAT_SOC | FLOAT (byte order: ABCD) | Battery SOC [%] | Not defined
21026..21027 | BAT_SOH | FLOAT (byte order: ABCD) | Battery SOH [%] | Not defined
21028..21029 | BAT_SOE | FLOAT (byte order: ABCD) | Battery SOE [Wh] | Not defined
21030..21031 | BAT_OCC | FLOAT (byte order: ABCD) | Battery Online Charge Capacity [kW] | Not defined
21032..21033 | BAT_ODC | FLOAT (byte order: ABCD) | Battery Online Discharge Capacity [kW] | Not defined
21034..21039 | MAC_ADDR | Char, 24 byte ASCII characters | EMS MAC address | Not defined
21040..21041 | BAT_STOP_ALL_CHARGING | FLOAT (byte order: ABCD) | Stop all charging SOC limit [%] | Not defined
21042..21043 | BAT_STOP_ALL_DISCHARGING | FLOAT (byte order: ABCD) | Stop all discharging SOC limit [%] | Not defined
21044..21045 | BAT_CHARGE_DG_START_SOC | FLOAT (byte order: ABCD) | Start charging battery with DG SOC limit [%] | Not defined
21046..21047 | BAT_CHARGE_DG_STOP_SOC | FLOAT (byte order: ABCD) | Stop charging battery with DG SOC limit [%] | Not defined
21048..21049 | BAT_CHARGE_MAINS_START_SOC | FLOAT (byte order: ABCD) | Start charging battery with Mains SOC limit [%] | Not defined
21050..21051 | BAT_CHARGE_MAINS_STOP_SOC | FLOAT (byte order: ABCD) | Stop charging battery with Mains SOC limit [%] | Not defined
21052..21053 | BAT_CHARGE_PV_START_SOC | FLOAT (byte order: ABCD) | Start charging battery with PV SOC limit [%] | Not defined
21054..21055 | BAT_CHARGE_PV_STOP_SOC | FLOAT (byte order: ABCD) | Stop charging battery with PV SOC limit [%] | Not defined
21056 | BAT_CHARGE_DG_ENA | 16 unsigned int | 0: DISABLED 1: ENABLED | Not defined
21057 | BAT_CHARGE_MAINS_ENA | 16 unsigned int | 0: DISABLED 1: ENABLED | Not defined
21058 | BAT_CHARGE_PV_ENA | 16 unsigned int | 0: DISABLED 1: ENABLED | Not defined
21059 | MAINS_P_CTRL_MODE | 16 unsigned int | 0: FIXED P 1: FIXED P PCC | Not defined
21060 | MAINS_BAT_P_CTRL_MODE | 16 unsigned int | 0: SYSTEM P 1: FIXED P | Not defined
21061 | MAINS_Q_CTRL_MODE | 16 unsigned int | 0: FIXED Q 1: FIXED Q PCC | Not defined
21062 | MAINS_BAT_Q_CTRL_MODE | 16 unsigned int | 0: SYSTEM Q 1: FIXED Q | Not defined
21063 | BAT_EVT01 | 16 unsigned int | 0: PV Started 1: PV Stopped 2: DG Started 3: DG Stopped 4: BAT Started 5: BAT Stopped 6: Grid Started 7: Grid Stopped 8: BAT Max OCC Limit Ena 9: BAT Max ODC Limit Ena 10: Battery Ready 11: Battery Running 12: AnyGBPosOn 13: AnyMBPosOn 14: BAT Charge Any Active | 0xFFFF
21064 | BAT_EVT02 | 16 unsigned int | 0: Simulation Active | 0xFFFF
ECLOGIC BUILDER AREA 1
28000 | Q1 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28001 | Q2 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28002 | Q3 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28003 | Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28004 | Inverted Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28005..28099 | RESERVED | Not defined | Reserved for later use | Not defined
ECLOGIC LINKER COMMAND AREA 1
29056 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise | Not defined
29057 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise | Not defined
29058 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise | Not defined
29059 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise | Not defined
29060 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise | Not defined
29061 | SOC Set flip flop 1-8 | 16 unsigned int | bitwise | Not defined
29062 | SOC Reset flip flop 1-8 | 16 unsigned int | bitwise | Not defined
29063..29065 | RESERVED | Not defined | Reserved for later use | Not defined
29066 | Cmd panel LED 01..16: Green | 16 unsigned int | bitwise | Not defined
29067 | Cmd panel LED 01..16: Red | 16 unsigned int | bitwise | Not defined
29068 | EClogic Alarms 01..08 | 16 unsigned int | bitwise | Not defined
29069 | EClogic Timers 01..08 | 16 unsigned int | bitwise | Not defined
29070..29075 | RESERVED | Not defined | Reserved for later use | Not defined
29076 | EClogic EV Power Limit Overwrite | 16 unsiged int | bitwise | Not defined
29076..29799 | RESERVED | Not defined | Reserved for later use | Not defined
MISC AREA 1
Address | DataLabel | DataType | Description | Not available value
30000..30001 | EMS_TOTAL_CAPACITY | FLOAT (byte order: ABCD) | Total EMS active power capacity [kW] | Not defined
30002..30003 | EMS_TOTAL_OUTPUT_POWER | FLOAT (byte order: ABCD) | Total EMS output power [kW] | Not defined
30004..30005 | EV_TOTAL_LOAD | FLOAT (byte order: ABCD) | Total loading from EV chargers [kW] | Not defined
30006..30007 | EV_TOTAL_LOAD_PCT | FLOAT (byte order: ABCD) | Total loading from EV chargers [%] | Not defined
30008..30009 | EMS_EXTERNAL_LOAD | FLOAT (byte order: ABCD) | Total EMS external load [kW] | Not defined
30010..30011 | EV_TOTAL_POWER_LIMIT | FLOAT (byte order: ABCD) | Total Power limit for EV chargers [kW] | Not defined
30012 | EV_MISSING_01_16 | 16 unsigned int | bitwise | Not defined
30013 | EV_MISSING_17_32 | 16 unsigned int | bitwise | Not defined
30014 | EV_NBROF_EV | 16 unsigned int | Number of EV charging stations | Not defined
30015 | EV_HIDE_EV_17_32 | 16 unsigned int | bitwise | Not defined
30016..30017 | EMS_LOAD_PCT | FLOAT (byte order: ABCD) | Total loading of the EMS [%] | Not defined
30018 | EV_NBROF_GUNS_PER_STATION01 | 16 unsigned int | Number of guns on EV charging station 1 | Not defined
30019 | EV_NBROF_GUNS_PER_STATION02 | 16 unsigned int | Number of guns on EV charging station 2 | Not defined
30020 | EV_NBROF_GUNS_PER_STATION03 | 16 unsigned int | Number of guns on EV charging station 3 | Not defined
30021 | EV_NBROF_GUNS_PER_STATION04 | 16 unsigned int | Number of guns on EV charging station 4 | Not defined
30022 | EV_NBROF_GUNS_PER_STATION05 | 16 unsigned int | Number of guns on EV charging station 5 | Not defined
30023 | EV_NBROF_GUNS_PER_STATION06 | 16 unsigned int | Number of guns on EV charging station 6 | Not defined
30024 | EV_NBROF_GUNS_PER_STATION07 | 16 unsigned int | Number of guns on EV charging station 7 | Not defined
30025 | EV_NBROF_GUNS_PER_STATION08 | 16 unsigned int | Number of guns on EV charging station 8 | Not defined
30026 | EV_NBROF_GUNS_PER_STATION09 | 16 unsigned int | Number of guns on EV charging station 9 | Not defined
30027 | EV_NBROF_GUNS_PER_STATION10 | 16 unsigned int | Number of guns on EV charging station 10 | Not defined
30028 | EV_NBROF_GUNS_PER_STATION11 | 16 unsigned int | Number of guns on EV charging station 11 | Not defined
30029 | EV_NBROF_GUNS_PER_STATION12 | 16 unsigned int | Number of guns on EV charging station 12 | Not defined
30030 | EV_NBROF_GUNS_PER_STATION13 | 16 unsigned int | Number of guns on EV charging station 13 | Not defined
30031 | EV_NBROF_GUNS_PER_STATION14 | 16 unsigned int | Number of guns on EV charging station 14 | Not defined
30032 | EV_NBROF_GUNS_PER_STATION15 | 16 unsigned int | Number of guns on EV charging station 15 | Not defined
30033 | EV_NBROF_GUNS_PER_STATION16 | 16 unsigned int | Number of guns on EV charging station 16 | Not defined
30034 | EV_NBROF_GUNS_PER_STATION17 | 16 unsigned int | Number of guns on EV charging station 17 | Not defined
30035 | EV_NBROF_GUNS_PER_STATION18 | 16 unsigned int | Number of guns on EV charging station 18 | Not defined
30036 | EV_NBROF_GUNS_PER_STATION19 | 16 unsigned int | Number of guns on EV charging station 19 | Not defined
30037 | EV_NBROF_GUNS_PER_STATION20 | 16 unsigned int | Number of guns on EV charging station 20 | Not defined
30038 | EV_NBROF_GUNS_PER_STATION21 | 16 unsigned int | Number of guns on EV charging station 21 | Not defined
30039 | EV_NBROF_GUNS_PER_STATION22 | 16 unsigned int | Number of guns on EV charging station 22 | Not defined
30040 | EV_NBROF_GUNS_PER_STATION23 | 16 unsigned int | Number of guns on EV charging station 23 | Not defined
30041 | EV_NBROF_GUNS_PER_STATION24 | 16 unsigned int | Number of guns on EV charging station 24 | Not defined
30042 | EV_NBROF_GUNS_PER_STATION25 | 16 unsigned int | Number of guns on EV charging station 25 | Not defined
30043 | EV_NBROF_GUNS_PER_STATION26 | 16 unsigned int | Number of guns on EV charging station 26 | Not defined
30044 | EV_NBROF_GUNS_PER_STATION27 | 16 unsigned int | Number of guns on EV charging station 27 | Not defined
30045 | EV_NBROF_GUNS_PER_STATION28 | 16 unsigned int | Number of guns on EV charging station 28 | Not defined
30046 | EV_NBROF_GUNS_PER_STATION29 | 16 unsigned int | Number of guns on EV charging station 29 | Not defined
30047 | EV_NBROF_GUNS_PER_STATION30 | 16 unsigned int | Number of guns on EV charging station 30 | Not defined
30048 | EV_NBROF_GUNS_PER_STATION31 | 16 unsigned int | Number of guns on EV charging station 31 | Not defined
30049 | EV_NBROF_GUNS_PER_STATION32 | 16 unsigned int | Number of guns on EV charging station 32 | Not defined
30050..30051 | ENERGY_EV_TOTAL | FLOAT (byte order: ABCD) | Total energy consumption from EV chargers [Wh] | Not defined
30052..30053 | ENERGY_EV_YEAR | FLOAT (byte order: ABCD) | This Years energy consumption from EV chargers [Wh] | Not defined
30054..30055 | ENERGY_EV_MONTH | FLOAT (byte order: ABCD) | This Months energy consumption from EV chargers [Wh] | Not defined
30056..30057 | ENERGY_EV_DAY | FLOAT (byte order: ABCD) | Todays energy consumption from EV chargers [Wh] | Not defined
30058..30545 | RESERVED | Not defined | Reserved for later use | Not defined
30546..30547 | LATITUDE | FLOAT (byte order: ABCD) | Latitude GPS coordinate | Not defined
30548..30549 | LONGITUDE | FLOAT (byte order: ABCD) | Longitude GPS coordinate | Not defined
30550..30998 | RESERVED | Not defined | Reserved for later use | Not defined
30999 | ECPV_SW_VERSION | 16 unsigned int | SW version opf the Ecpv application SW
BITFIELD AREA 1
31000 | BITFIELD_1 | 16 unsigned int | BIT0: EV Started BIT1: EV Stopped BIT2: Simulation Enabled BIT3: Any EV missing BIT4: EV socket conn. alarm BIT5: EV comm alarm | Not defined
31001 | BITFIELD_2 | 16 unsigned int | EV missing 01-16 | Not defined
31002 | BITFIELD_3 | 16 unsigned int | EV missing 17-32 | Not defined
31003 | BITFIELD_4 | 16 unsigned int | BIT13: COM2 slave timeout BIT14: COM3 slave timeout BIT15: TCP slave timeout | Not defined
31004 | BITFIELD_5 | 16 unsigned int | BIT0: Event log FTP fail BIT3: Test FTP fail | Not defined
31005 | BITFIELD_6 | 16 unsigned int | BIT4: Comm 2 slave timeout alarm BIT5: Comm 3 slave timeout alarm BIT6: TCP slave timeout alarm | Not defined
31013 | BITFIELD_14 | 16 unsigned int | BIT0: IO module 1 missing BIT1: IO module 2 missing BIT2: IO module 3 missing BIT3: IO module 4 missing | Not defined
31014 | BITFIELD_15 | 16 unsigned int | EClogic Threshold output 01..16 | Not defined
31018 | BITFIELD_19 | 16 unsigned int | BIT0: Command timer 01 active BIT1: Command timer 02 active BIT2: Command timer 03 active BIT3: Command timer 04 active BIT4: DG charge timer active BIT5: Mains charge timer active BIT6: Mains charge scheduler, charge enabled BIT7: Dispatch power when DG connected disabled BIT8: Dispatch power when grid is connected disabled BIT9: Mains charge scheduler, discharge enabled BIT10: Mains spotprice optimizer, charge enabled BIT11: Mains spotprice optimizer, discharge enabled | Not defined
31021 | BITFIELD_22 | 16 unsigned int | EClogic Timers elapsed 01..16 | Not defined
31022 | BITFIELD_23 | 16 unsigned int | EClogic Modbus Event 01..16 | Not defined
31023 | BITFIELD_24 | 16 unsigned int | EClogic Modbus Event 17..32 | Not defined
31024 | BITFIELD_25 | 16 unsigned int | BIT0: EClogic alarm 01 active BIT1:EClogic alarm 02 active BIT2: EClogic alarm 03 active BIT3: EClogic alarm 04 active BIT4: EClogic alarm 05 active BIT5:EClogic alarm 06 active BIT6: EClogic alarm 07 active BIT7: EClogic alarm 08 active | Not defined
SETTINGS AREA
31700 | NBR_OF_EV | 16 unsigned int | Number of EV charging stations | Not defined
31701..31702 | INSTALLED_EV_CAPACITY | 32 signed int (byte order: ABCD) | Total installed EV capacity [kW] | Not defined
31703 | EV_TYPE | 16 unsigned int | Type of EV charging stations | Not defined
31704 | CTRL_OF_EV_ENA | 16 unsigned int | 0: DISABLED 1: ENABLED | Not defined
31705..31729 | RESERVED | Not defined | Reserved for later use | Not defined
31730 | IOS_ENABLED | 16 unsigned int | Bitwise 0: IO module 1 1: IO module 2 2: IO module 3 3: IO module 4 | Not defined
RTC CLOCK
32000 | Year | 16 unsigned int | ECpv RTC year | Not defined
32001 | Month | 16 unsigned int | ECpv RTC month | Not defined
32002 | Date | 16 unsigned int | ECpv RTC date | Not defined
32003 | Hour | 16 unsigned int | ECpv RTC hour | Not defined
32004 | Minute | 16 unsigned int | ECpv RTC minute | Not defined
32005 | Second | 16 unsigned int | ECpv RTC second | Not defined
32006 | Millisecond | 16 unsigned int | ECpv RTC millisecond | Not defined
IO MODULE INFO
32010 | IO_TYPE_01 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32011 | IO_TYPE_02 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32012 | IO_TYPE_03 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32013 | IO_TYPE_04 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32014 | IO_ANALOGUE_TYPE_SELECTED | 16 unsigned int | BIT0: Module 1 is analogue type BIT1: Module 2 is analogue type BIT2: Module 3 is analogue type BIT3: Module 4 is analogue type
32020..32039 | INFOTEXT_MODULE_01 | string | Info text for Module 1 type | Not defined
32040..32059 | INFOTEXT_MODULE_02 | string | Info text for Module 2 type | Not defined
32060..32079 | INFOTEXT_MODULE_03 | string | Info text for Module 3 type | Not defined
32080..32099 | INFOTEXT_MODULE_04 | string | Info text for Module 4 type | Not defined
STAUS TEXTS
32400..32479 | STATUS_TEXT_01 | string | Status text in line 1 | Not defined
32480..32559 | STATUS_TEXT_02 | string | Status text in line 2 | Not defined
32560..32639 | STATUS_TEXT_03 | string | Status text in line 3 | Not defined
32640 | STATUS_TEXT_01_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32641 | STATUS_TEXT_02_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32642 | STATUS_TEXT_03_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32643 | NBR_OF_STATUS_TEXTS | 16 unsigned int | Number of status texts displayed | Not defined
32644 | MIN_SLIDER | 16 signed int | Minimum possible status text slider value | Not defined

## Holding Register 0x03
Proprietary profile
Address | DataLabel | DataType | Description | Note
1000 | EV_START | 16 unsigned int | 0: STOP 1: START | Not defined

## Coils 0x01
Proprietary profile
Address | DataLabel | DataType | Description | Note
Page05 (DNP3 control) |  |  |  | Page05 needs to be enabled