## Input Register 0x04
Battery inverter Acquisition 1 to 32 The addressses of inverter number x is found by: AddressModule_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
10000..10015 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
10016..10031 | MODEL | Char, 32 byte Ascii characters | Inverter model | Not defined
10032..10039 | VERSION | Char, 16 byte Ascii characters | Version | Not defined
10040..10099 | RESERVED | Not defined | Reserved for later use | Not defined
10100..10101 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
10102..10103 | ACP L1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
10104..10105 | ACP L2 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
10106..10107 | ACP L3 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
10108..10109 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
10110..10111 | ACQ L1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
10112..10113 | ACQ L2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
10114..10115 | ACQ L3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
10116..10117 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
10118..10119 | ACS L1 | 32 signed int (byte order: ABCD) | AC Apparent power line1 [VA] | 0x80000000
10120..10121 | ACS L2 | 32 signed int (byte order: ABCD) | AC Apparent power line2 [VA] | 0x80000000
10122..10123 | ACS L3 | 32 signed int (byte order: ABCD) | AC Apparent power line3 [VA] | 0x80000000
10124 | PF | 16 signed int | Power factor total [0.001] | 0x8000
10125 | PF L1 | 16 signed int | Power factor line1 [0.001] | 0x8000
10126 | PF L2 | 16 signed int | Power factor line2 [0.001] | 0x8000
10127 | PF L3 | 16 signed int | Power factor line3 [0.001] | 0x8000
10128..10129 | WH | 32 unsigned int (byte order: ABCD) | Energy total [kWh] | 0xFFFFFFFF
10130..10131 | WH_IMP | 32 unsigned int (byte order: ABCD) | Energy total import [0.1kWh] | 0xFFFFFFFF
10132 | L1N | 16 unsigned int | Line1-neutral voltage [0.1V] | 0xFFFF
10133 | L2N | 16 unsigned int | Line2-neutral voltage [0.1V] | 0xFFFF
10134 | L3N | 16 unsigned int | Line3-neutral voltage [0.1V] | 0xFFFF
10135 | L1L2 | 16 unsigned int | Line1-line2 voltage [0.1V] | 0xFFFF
10136 | L2L3 | 16 unsigned int | Line2-line3 voltage [0.1V] | 0xFFFF
10137 | L3L1 | 16 unsigned int | Line3-line1 voltage [0.1V] | 0xFFFF
10138 | L1A | 16 unsigned int | line1 current [0.1A] | 0xFFFF
10139 | L2A | 16 unsigned int | line2 current [0.1A] | 0xFFFF
10140 | L3A | 16 unsigned int | line3 current [0.1A] | 0xFFFF
10141 | LNA | 16 unsigned int | Neutral current [0.1A] | 0xFFFF
10142 | FL1 | 16 unsigned int | L1 frequency [0.01Hz] | 0xFFFF
10143 | FL2 | 16 unsigned int | L2 frequency [0.01Hz] | 0xFFFF
10144 | FL3 | 16 unsigned int | L3 frequency [0.01Hz] | 0xFFFF
10145 | CAB_TEMP | 16 signed int | Cabinet temperature [0.1C] | 0x8000
10146 | STATE | 16 unsigned int | Inverter state | 0xFFFF
10147 | DCA1 | 16 signed int | DC currrent input 1 [0.1A] | 0xFFFF
10148 | DCU1 | 16 unsigned int | DC voltage input 1 [0.1V] | 0xFFFF
10149 | DCP1 | 16 signed int | DC power input 1 [0.1kW] | 0x8000
10150 | DCA2 | 16 signed int | DC currrent input 2 [0.1A] | 0xFFFF
10151 | DCU2 | 16 unsigned int | DC voltage input 2 [0.1V] | 0xFFFF
10152 | DCP2 | 16 signed int | DC power input 2 [0.1kW] | 0x8000
10153..10154 | EVT1 | 32 unsigned int (byte order: ABCD) | Event field 1 | 0xFFFFFFFF
10155..10156 | EVT2 | 32 unsigned int (byte order: ABCD) | Event field 2 | 0xFFFFFFFF
10157..10158 | EVT3 | 32 unsigned int (byte order: ABCD) | Event field 3 | 0xFFFFFFFF
10159..10160 | EVT4 | 32 unsigned int (byte order: ABCD) | Event field 4 | 0xFFFFFFFF
10161 | SOC | 16 unsigned int | State of charge [0.1%] | Not defined
10162..10163 | SOE | 32 unsigned int (byte order: ABCD) | State of energy [0.1kWh] | Not defined
10164 | SOH | 16 unsigned int | State of health [0.1%] | Not defined
10165..10166 | OCC | 32 unsigned int (byte order: ABCD) | Online charging capacity [0.1kW] | Not defined
10167..10168 | OGC | 32 unsigned int (byte order: ABCD) | Online discharging capacity [0.1kW] | Not defined
10169 | MIN CELL VOLTAGE | 16 unsigned int | Minimum cell voltage [mV] | Not defined
10170 | MAX CELL VOLTAGE | 16 unsigned int | Maximum cell voltage [mV] | Not defined
10171 | MIN CELL TEMPERATURE | 16 signed int | Minimum temperature voltage [0.1C] | Not defined
10172 | MAX CELL TEMPERATURE | 16 signed int | Maximum temperature voltage [0.1C] | Not defined
10173 | BMS_STATE | 16 unsigned int | BMS state | Not defined
10174..10198 | RESERVED | Not defined | Reserved for later use | Not defined
10199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Battery Cluster
21300..21301 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
21302..21303 | ACP L1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
21304..21305 | ACP L2 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
21306..21307 | ACP L3 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
21308..21309 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
21310..21311 | ACQ L1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
21312..21313 | ACQ L2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
21314..21315 | ACQ L3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
21316..21317 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
21318..21319 | ACS L1 | 32 signed int (byte order: ABCD) | AC Apparent power line1 [VA] | 0x80000000
21320..21321 | ACS L2 | 32 signed int (byte order: ABCD) | AC Apparent power line2 [VA] | 0x80000000
21322..21323 | ACS L3 | 32 signed int (byte order: ABCD) | AC Apparent power line3 [VA] | 0x80000000
21324 | PF | 16 signed int | Power factor total [0.001] | 0x8000
21325 | PF L1 | 16 signed int | Power factor line1 [0.001] | 0x8000
21326 | PF L2 | 16 signed int | Power factor line2 [0.001] | 0x8000
21327 | PF L3 | 16 signed int | Power factor line3 [0.001] | 0x8000
21328..21329 | WH | 32 unsigned int (byte order: ABCD) | Energy total [kWh] | 0xFFFFFFFF
21330..21331 | WH_IMP | 32 unsigned int (byte order: ABCD) | Energy total import [0.1kWh] | 0xFFFFFFFF
21332 | L1N | 16 unsigned int | Line1-neutral voltage [0.1V] | 0xFFFF
21333 | L2N | 16 unsigned int | Line2-neutral voltage [0.1V] | 0xFFFF
21334 | L3N | 16 unsigned int | Line3-neutral voltage [0.1V] | 0xFFFF
21335 | L1L2 | 16 unsigned int | Line1-line2 voltage [0.1V] | 0xFFFF
21336 | L2L3 | 16 unsigned int | Line2-line3 voltage [0.1V] | 0xFFFF
21337 | L3L1 | 16 unsigned int | Line3-line1 voltage [0.1V] | 0xFFFF
21338 | L1A | 16 unsigned int | line1 current [0.1A] | 0xFFFF
21339 | L2A | 16 unsigned int | line2 current [0.1A] | 0xFFFF
21340 | L3A | 16 unsigned int | line3 current [0.1A] | 0xFFFF
21341 | LNA | 16 unsigned int | Neutral current [0.1A] | 0xFFFF
21342 | FL1 | 16 unsigned int | L1 frequency [0.01Hz] | 0xFFFF
21343 | FL2 | 16 unsigned int | L2 frequency [0.01Hz] | 0xFFFF
21344 | FL3 | 16 unsigned int | L3 frequency [0.01Hz] | 0xFFFF
21345 | CAB_TEMP | 16 signed int | Cabinet temperature [0.1C] | 0x8000
21346 | STATE | 16 unsigned int | BIT0: Any battery ready BIT1: Any battery running BIT2: Any STS open BIT3: All emergency stop BIT4: Reserved BIT5: Any battery faulted BIT6: Battery comm. alarm / Socket alarm BIT7: Ready PQ Mode BIT8: Ready VF Mode BIT9: SOC balancing request BIT10: Any battery PCS missing BIT11: All battery PCS missing | 0xFFFF
21347 | DCA1 | 16 signed int | DC currrent input 1 [0.1A] | 0xFFFF
21348 | DCU1 | 16 unsigned int | DC voltage input 1 [0.1V] | 0xFFFF
21349 | DCP1 | 16 signed int | DC power input 1 [0.1kW] | 0x8000
21350 | DCA2 | 16 signed int | DC currrent input 2 [0.1A] | 0xFFFF
21351 | DCU2 | 16 unsigned int | DC voltage input 2 [0.1V] | 0xFFFF
21352 | DCP2 | 16 signed int | DC power input 2 [0.1kW] | 0x8000
21353..21354 | EVT1 | 32 unsigned int (byte order: ABCD) | Event field 1 | 0xFFFFFFFF
21355..21356 | EVT2 | 32 unsigned int (byte order: ABCD) | Event field 2 | 0xFFFFFFFF
21357..21358 | EVT3 | 32 unsigned int (byte order: ABCD) | Event field 3 | 0xFFFFFFFF
21359..21360 | EVT4 | 32 unsigned int (byte order: ABCD) | Event field 4 | 0xFFFFFFFF
21361 | SOC | 16 unsigned int | State of charge [0.1%] | Not defined
21362..21363 | SOE | 32 unsigned int (byte order: ABCD) | State of energy [0.1kWh] | Not defined
21364 | SOH | 16 unsigned int | State of health [0.1%] | Not defined
21365..21366 | OCC | 32 unsigned int (byte order: ABCD) | Online charging capacity [0.1kW] | Not defined
21367..21368 | OGC | 32 unsigned int (byte order: ABCD) | Online discharging capacity [0.1kW] | Not defined
21369 | MIN CELL VOLTAGE | 16 unsigned int | Minimum cell voltage [mV] | Not defined
21370 | MAX CELL VOLTAGE | 16 unsigned int | Maximum cell voltage [mV] | Not defined
21371 | MIN CELL TEMPERATURE | 16 signed int | Minimum temperature voltage [0.1C] | Not defined
21372 | MAX CELL TEMPERATURE | 16 signed int | Maximum temperature voltage [0.1C] | Not defined
21373 | BMS_STATE | 16 unsigned int | BMS state | Not defined
21374..21398 | RESERVED | Not defined | Reserved for later use | Not defined
21399 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
IO module number 1 to 4 The addressses of module number x is found by: AddressModule_x = (x-1) * 50 + Address
Address | DataLabel | DataType | Description | Not available value
20500 | INPUT_1_16 | 16 unsigned int | bitwise | Not defined
20501 | OUTPUT_1_16 | 16 unsigned int | bitwise | Not defined
20502..20503 | AIO_INPUT_01 | FLOAT (byte order: ABCD) | Analogue input 01 | Not defined
20504..20505 | AIO_INPUT_02 | FLOAT (byte order: ABCD) | Analogue input 02 | Not defined
20506..20507 | AIO_INPUT_03 | FLOAT (byte order: ABCD) | Analogue input 03 | Not defined
20508-20509 | AIO_INPUT_04 | FLOAT (byte order: ABCD) | Analogue input 04 | Not defined
20510..20511 | AIO_INPUT_05 | FLOAT (byte order: ABCD) | Analogue input 05 | Not defined
20512..20513 | AIO_INPUT_06 | FLOAT (byte order: ABCD) | Analogue input 06 | Not defined
20514..20515 | AIO_INPUT_07 | FLOAT (byte order: ABCD) | Analogue input 07 | Not defined
20516..20517 | AIO_INPUT_08 | FLOAT (byte order: ABCD) | Analogue input 08 | Not defined
20518..20519 | AIO_OUTPUT_01 | FLOAT (byte order: ABCD) | Analogue output 01 | Not defined
20520..20521 | AIO_OUTPUT_02 | FLOAT (byte order: ABCD) | Analogue output 02 | Not defined
20522..20523 | AIO_OUTPUT_03 | FLOAT (byte order: ABCD) | Analogue output 03 | Not defined
20524..20525 | AIO_OUTPUT_04 | FLOAT (byte order: ABCD) | Analogue output 04 | Not defined
20526..20527 | AIO_OUTPUT_05 | FLOAT (byte order: ABCD) | Analogue output 05 | Not defined
20528..20529 | AIO_OUTPUT_06 | FLOAT (byte order: ABCD) | Analogue output 06 | Not defined
20530..20531 | AIO_OUTPUT_07 | FLOAT (byte order: ABCD) | Analogue output 07 | Not defined
20532..20533 | AIO_OUTPUT_08 | FLOAT (byte order: ABCD) | Analogue output 08 | Not defined
20534 | CH_CONF_01 | 16 unsigned int | Channel confirguration 01 | Not defined
20535 | CH_CONF_02 | 16 unsigned int | Channel confirguration 02 | Not defined
20536 | CH_CONF_03 | 16 unsigned int | Channel confirguration 03 | Not defined
20537 | CH_CONF_04 | 16 unsigned int | Channel confirguration 04 | Not defined
20538 | CH_CONF_05 | 16 unsigned int | Channel confirguration 05 | Not defined
20539 | CH_CONF_06 | 16 unsigned int | Channel confirguration 06 | Not defined
20540 | CH_CONF_07 | 16 unsigned int | Channel confirguration 07 | Not defined
20541 | CH_CONF_08 | 16 unsigned int | Channel confirguration 08 | Not defined
20542 | CH_STATUS | 16 unsigned int | Channel status | Not defined
20543 | MOD_TEMP | 16 unsigned int | Module temperature [0.1C] | Not defined
20544..20548 | RESERVED | Not defined | Reserved for later use | Not defined
20549 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
COMMAND PANEL TEXTS
27000..27079 | TEXT_CMD_PANEL_BUTTON 01..04 | string | User configurable texts for command panel button 01..04 | Not defined
27080..27159 | TEXT_CMD_PANEL_BUTTON 05..08 | string | User configurable texts for command panel button 05..08 | Not defined
27160..27239 | TEXT_CMD_PANEL_BUTTON 09..12 | string | User configurable texts for command panel button 09..12 | Not defined
27240..27319 | TEXT_CMD_PANEL_BUTTON 13..16 | string | User configurable texts for command panel button 13..16 | Not defined
27320..27399 | TEXT_CMD_PANEL_LED 01..04 | string | User configurable texts for command panel led 01..04 | Not defined
27400..27479 | TEXT_CMD_PANEL_LED 05..08 | string | User configurable texts for command panel led 05..08 | Not defined
27480..27559 | TEXT_CMD_PANEL_LED 09..12 | string | User configurable texts for command panel led 09..12 | Not defined
27560..27639 | TEXT_CMD_PANEL_LED 13..16 | string | User configurable texts for command panel led 13..16 | Not defined
27640..27999 | RESERVED | Not defined | Reserved for later use | Not defined
ECLOGIC BUILDER AREA 1
28000 | Q1 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28001 | Q2 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28002 | Q3 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28003 | Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28004 | Inverted Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28005..28999 | RESERVED | Not defined | Reserved for later use | Not defined
ECLOGIC LINKER COMMAND AREA 1
29000 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise | Not defined
29001 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise | Not defined
29002 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise | Not defined
29003 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise | Not defined
29004 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise | Not defined
29005 | Cmd panel LED01..16: Green | 16 unsigned int | bitwise | Not defined
29006 | Cmd panel LED01..16: Red | 16 unsigned int | bitwise | Not defined
29007..29999 | RESERVED | Not defined | Reserved for later use | Not defined
MISC AREA 1
30000..30001 | LATITUDE | FLOAT (byte order: ABCD) | Latitude GPS coordinate | Not defined
30002..30003 | LONGITUDE | FLOAT (byte order: ABCD) | Longitude GPS coordinate | Not defined
30504..30005 | POWER_P_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery active power [kW] | Not defined
30006..30007 | POWER_Q_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery reactive power [kVAr] | Not defined
30008..30009 | POWER_S_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery apparent power [kVA] | Not defined
30010..30011 | COSPHI_BAT_TOTAL | FLOAT (byte order: ABCD) | Cosphi Battery [%] | Not defined
30012 | COSPHI_BAT_IND_CAP | 16 unsigned int | Cosphi capacitive | Not defined
30013..30014 | BATTERY_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Battery inverter generating capacity active power [kW] | Not defined
30015..30016 | BATTERY_Q_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Battery inverter generating capacity reactive power [kVAr] | Not defined
30017..30018 | BATTERY_P_POWER_TARGET | FLOAT (byte order: ABCD) | Active Power Battery Reference [kW] | Not defined
30019..30020 | BATTERY_P_POWER_REFERENCE | FLOAT (byte order: ABCD) | Active Power Battery Reference Ramped [kW] | Not defined
30021..30022 | BATTERY_Q_POWER_TARGET | FLOAT (byte order: ABCD) | Reactive Power Battery Reference [kW] | Not defined
30023..30024 | BATTERY_Q_POWER_REFERENCE | FLOAT (byte order: ABCD) | Reactive Power Battery Reference Ramped [kW] | Not defined
30625..30026 | P_BATTERY_LOAD_PCT | FLOAT (byte order: ABCD) | Battery active power loading [%] | Not defined
30027..30028 | Q_BATTERY_LOAD_PCT | FLOAT (byte order: ABCD) | Battery reactive power loading [%] | Not defined
30029..30030 | P_BATTERY_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Battery active power error in regards to refernce [%] | Not defined
30031..30032 | Q_BATTERY_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Battery reactive power error in regards to refernce [%] | Not defined
30033..30034 | BATTERY_SOC_PCT | FLOAT (byte order: ABCD) | Battery State Of Charge [%] | Not defined
30035..30036 | BATTERY_SOH_PCT | FLOAT (byte order: ABCD) | Battery State Of Health [%] | Not defined
30037..30038 | BATTERY_SOE_KWH | FLOAT (byte order: ABCD) | Battery State Of Energy [kWh] | Not defined
30039..30040 | BATTERY_ODC_KW | FLOAT (byte order: ABCD) | Battery online discharge capacity [kW] | Not defined
30041..30042 | BATTERY_OCC_KW | FLOAT (byte order: ABCD) | Battery online charge capacity [kW] | Not defined
30043..30044 | BATTERY_EFC_TOTAL | FLOAT (byte order: ABCD) | EFC counter total | Not defined
30045..30046 | BATTERY_EFC_YEAR | FLOAT (byte order: ABCD) | EFC counter year | Not defined
30047..30048 | BATTERY_EFC_MONTH | FLOAT (byte order: ABCD) | EFC counter month | Not defined
30049..30050 | BATTERY_EFC_DAY | FLOAT (byte order: ABCD) | EFC counter day | Not defined
30051..30052 | BATTERY_DOD_TOTAL | FLOAT (byte order: ABCD) | DOD counter total | Not defined
30053..30054 | BATTERY_DOD_YEAR | FLOAT (byte order: ABCD) | DOD counter year | Not defined
30055..30056 | BATTERY_DOD_MONTH | FLOAT (byte order: ABCD) | DOD counter month | Not defined
30057..30058 | BATTERY_DOD_DAY | FLOAT (byte order: ABCD) | DOD counter day | Not defined
30059..30060 | BATTERY_ENERGY_TOTAL | FLOAT (byte order: ABCD) | Battery energy total [kWh] | Not defined
30061..30062 | BATTERY_ENERGY_YEAR | FLOAT (byte order: ABCD) | Battery energy year [kWh] | Not defined
30063..30064 | BATTERY_ENERGY_MONTH | FLOAT (byte order: ABCD) | Battery energy month [kWh] | Not defined
30065..30066 | BATTERY_ENERGY_DAY | FLOAT (byte order: ABCD) | Battery energy day [kWh] | Not defined
30067..30068 | BATTERY_IMP_TOTAL | FLOAT (byte order: ABCD) | Battery imported total [kWh] | Not defined
30069..30070 | BATTERY_IMP_YEAR | FLOAT (byte order: ABCD) | Battery imported year [kWh] | Not defined
30071..30072 | BATTERY_IMP_MONTH | FLOAT (byte order: ABCD) | Battery imported month [kWh] | Not defined
30073..30074 | BATTERY_IMP_DAY | FLOAT (byte order: ABCD) | Battery imported day [kWh] | Not defined
30076..30699 | Reserved
30699 | ECPV_SW_VERSION | 16 unsigned int | SW version opf the Ecpv application SW
Inverter 1 to 32 The addressses of inverter number x is found by: Address_x = (x-1) * 2 + Address
30700..30763 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30764..30827 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
BITFIELD AREA 1
31000 | BITFIELD_0 | 16 unsigned int | BIT0: COM2 slave timeout BIT1: COM3 slave timeout BIT2: TCP slave timeout BIT3: Common comm alarm | Not defined
31001 | BITFIELD_1 | 16 unsigned int | BIT0: Event log FTP fail BIT1: Test FTP fail BIT2: Event log mail fail BIT3: Test mail fail | Not defined
31002 | BITFIELD_2 | 16 unsigned int | ECpvX slave 01..16 missing | Not defined
31003 | BITFIELD_3 | 16 unsigned int | ECpvX slave 17..32 missing | Not defined
31004 | BITFIELD_4 | 16 unsigned int | BIT0: Any Battery inverter missing BIT1: Battery inverter socket connection alarm BIT2: Any ECpvX slave Bat inverter missing BIT3: All ECpvX slave Bat inverter missing | Not defined
31005 | BITFIELD_5 | 16 unsigned int | BIT0: IO module 1 missing BIT1: IO module 2 missing BIT2: IO module 3 missing BIT3: IO module 4 missing | Not defined
31006 | BITFIELD_6 | 16 unsigned int | BIT0: Command timer 01 active BIT1: Command timer 02 active BIT2: Command timer 03 active BIT3: Command timer 04 active | Not defined
31007 | BITFIELD_7 | 16 unsigned int | Command Panel buttons 01..16 | Not defined
31008 | BITFIELD_8 | 16 unsigned int | ECpvX slave bat inverter 1..16 missing | Not defined
31008 | BITFIELD_9 | 16 unsigned int | ECpvX slave bat inverter 17..32 missing | Not defined
RTC CLOCK
32000 | Year | 16 unsigned int | ECpv RTC year | Not defined
32001 | Month | 16 unsigned int | ECpv RTC month | Not defined
32002 | Date | 16 unsigned int | ECpv RTC date | Not defined
32003 | Hour | 16 unsigned int | ECpv RTC hour | Not defined
32004 | Minute | 16 unsigned int | ECpv RTC minute | Not defined
32005 | Second | 16 unsigned int | ECpv RTC second | Not defined
32006 | Millisecond | 16 unsigned int | ECpv RTC millisecond | Not defined
IO MODULE INFO
32010 | IO_TYPE_01 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32011 | IO_TYPE_02 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32012 | IO_TYPE_03 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32013 | IO_TYPE_04 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32014 | IO_ANALOGUE_TYPE_SELECTED | 16 unsigned int | BIT0: Module 1 is analogue type BIT1: Module 2 is analogue type BIT2: Module 3 is analogue type BIT3: Module 4 is analogue type
32020..32039 | INFOTEXT_MODULE_01 | string | Info text for Module 1 type | Not defined
32040..32059 | INFOTEXT_MODULE_02 | string | Info text for Module 2 type | Not defined
32060..32079 | INFOTEXT_MODULE_03 | string | Info text for Module 3 type | Not defined
32080..32099 | INFOTEXT_MODULE_04 | string | Info text for Module 4 type | Not defined
INFO&MODE TEXT
32100..32119 | INFOTEXT_BATTERY | string | Info text for Battery | Not defined
32120..32139 | MODETEXT_BATTERY | string | Mode text for Battery | Not defined
SETTINGS AREA
40000..40004 | CURRENCY | string | Currency | Not defined
40005..40009 | VOLUME | string | Volume | Not defined
40010..40014 | MASS | string | Mass | Not defined
40015 | IOS_ENABLED | 16 unsigned int | Bitwise 0: IO module 1 1: IO module 2 2: IO module 3 3: IO module 4 | Not defined
40016 | BAT_CONTROL | Enum | Battery control enabled 0: DISABLED 1: ENABLED | Not defined
40017 | NBR_BAT_INVERTERS | 16 unsigned int | Number of battery inverters | Not defined
40018/40019 | INSTALLED_S_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery inverter capacity in kVA | Not defined
40020/40021 | INSTALLED_Q_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery inverter capacity in kVAr | Not defined
40022/40023 | INSTALLED_P_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery capacity in kW | Not defined
40024/40025 | INSTALLED_H_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery capacity in hours | Not defined
STAUS TEXTS
41000..41079 | STATUS_TEXT_01 | string | Status text in line 1 | Not defined
41080..41159 | STATUS_TEXT_02 | string | Status text in line 2 | Not defined
41160..41239 | STATUS_TEXT_03 | string | Status text in line 3 | Not defined
41240 | STATUS_TEXT_01_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
41241 | STATUS_TEXT_02_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
41242 | STATUS_TEXT_03_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
41243 | NBR_OF_STATUS_TEXTS | 16 unsigned int | Number of status texts displayed | Not defined
41244 | MIN_SLIDER | 16 signed int | Minimum possible status text slider value | Not defined

## Holding Register 0x03
Proprietary profile
Address | DataLabel | DataType | Description | Note
Page01 (Commands) |  |  |  | Page01 need to be enabled
0 | Reserved
1 | Ack. All alarms. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
2 | Ack. All alarm in line 01. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
3 | Ack. All alarm in line 02. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
4 | Ack. All alarm in line 03. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
5 | Alarm slider | 16 signed int |  | Alarm slider control
6 | Year | 16 unsigned int | Set ECpv RTC year
7 | Month | 16 unsigned int | Set ECpv RTC month
8 | Date | 16 unsigned int | Set ECpv RTC date
9 | Hour | 16 unsigned int | Set ECpv RTC hour
10 | Minute | 16 unsigned int | Set ECpv RTC minute
11 | Second | 16 unsigned int | Set ECpv RTC second
12 | Millisecond | 16 unsigned int | Set ECpv RTC millisecond
13 | Set Ecpv RTC | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
14 | Cmd Panel buttons 01..16 | 16 unsigned int | bitwise
15..999 | Reserved
Page02 (Relay control) |  |  |  | Page02 needs to be enabled
1000 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise
1001 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise
1002 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise
1003 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise
1004 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise
1005..1999 | Reserved
Superior Control
5000 | START | enum16 | 0: Stop 1: Start
5001 | PREF | 16 signed int | Active power reference [-100.00%..100.00%]
5002 | QREF | 16 signed int | Reactive power reference [-100.00%..100.00%]
5003..5004 | Reserved
5005 | PCS_MODE | enum16 | 1: PQ 2: VF 3: VSG

## Coils 0x01
Proprietary profile
Address | DataLabel | DataType | Description | Note
Page05 (DNP3 control) |  |  |  | Page05 needs to be enabled
4000 | PV Ctrl. Active | Boolean | Superior power control from DNP3 (page05) active
4001 | PV Ramp Ctrl. Active | Boolean | Superior power ramp control from DNP3 (page05) active
4002..4999 | Reserved