## Input Register 0x04
Genset Power meter number 1 to 16 The addressses of genset meter number x is found by: AddressMeter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
0..1 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
2..3 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
4..5 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
6..7 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
8..9 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
10..11 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
12..13 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
14..15 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
16..17 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
18..19 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
20..21 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
22..23 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
24..25 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
26..27 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
28..29 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
30..31 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
32..33 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
34..35 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
36..37 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
38..39 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
40..41 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
42..43 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
44..45 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
46..47 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
48..49 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
50..51 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
52..53 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
54..55 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
56..57 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
58..59 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
60..61 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
62..63 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
64..65 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
66..67 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
68..69 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
70..196 | RESERVED | Not defined | Reserved for later use | Not defined
197 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
198 | GB_POSITION | 16 unsigned int | 0: GB Off 1: GB On | Not defined
199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
PV Power meter number 1 to 16 The addressses of PV meter number x is found by: AddressMeter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
3200..3201 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
3202..3203 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
3204..3205 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
3206..3207 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
3208..3209 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
3210..3211 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
3212..3213 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
3214..3215 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
3216..3217 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
3218..3219 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
3220..3221 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
3222..3223 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
3224..3225 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
3226..3227 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
3228..3229 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
3230..3231 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
3232..3233 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
3234..3235 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
3236..3237 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
3238..3239 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
3240..3241 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
3242..3243 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
3244..3245 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
3246..3247 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
3248..3249 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
3250..3251 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
3252..3253 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
3254..3255 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
3256..3257 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
3258..3259 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
3260..3261 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
3262..3263 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
3264..3265 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
3266..3267 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
3268..3269 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
3270..3396 | RESERVED | Not defined | Reserved for later use | Not defined
3397 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
3398 | RESERVED | Not defined | Reserved for later use | Not defined
3399 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Mains Power meter number 1 to 16 The addressses of Mains meter number x is found by: AddressMeter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
6400..6401 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
6402..6403 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
6404..6405 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
6406..6407 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
6408..6409 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
6410..6411 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
6412..6413 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
6414..6415 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
6416..6417 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
6418..6419 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
6420..6421 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
6422..6423 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
6424..6425 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
6426..6427 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
6428..6429 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
6430..6431 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
6432..6433 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
6434..6435 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
6436..6437 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
6438..6439 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
6440..6441 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
6442..6443 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
6444..6445 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
6446..6447 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
6448..6449 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
6450..6451 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
6452..6453 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
6454..6455 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
6456..6457 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
6458..6459 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
6460..6461 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
6462..6463 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
6464..6465 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
6466..6467 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
6468..6469 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
6470..6596 | RESERVED | Not defined | Reserved for later use | Not defined
6597 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
6598 | MB_POSITION | 16 unsigned int | 0: MB Off 1: MB On | Not defined
6599 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Inverter number 1 to 32 The addressses of Inverter number x is found by: AddressInverter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
10000..10015 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
10016..10031 | MODEL | Char, 32 byte Ascii characters | Inverter model | Not defined
10032..10039 | VERSION | Char, 16 byte Ascii characters | Version | Not defined
10040..10099 | RESERVED | Not defined | Reserved for later use | Not defined
10100..10101 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
10102..10103 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
10104..10105 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
10106 | PF | 16 signed int | Power factor total [0.001] | 0x8000
10107 | L1N | 16 unsigned int | Line1-neutral voltage [0.1V] | 0xFFFF
10108 | L2N | 16 unsigned int | Line2-neutral voltage [0.1V] | 0xFFFF
10109 | L3N | 16 unsigned int | Line3-neutral voltage [0.1V] | 0xFFFF
10110 | L1L2 | 16 unsigned int | Line1-line2 voltage [0.1V] | 0xFFFF
10111 | L2L3 | 16 unsigned int | Line2-line3 voltage [0.1V] | 0xFFFF
10112 | L3L1 | 16 unsigned int | Line3-line1 voltage [0.1V] | 0xFFFF
10113 | RESERVED | Not defined | Reserved for later use | Not defined
10114 | L1A | 16 unsigned int | line1 current [0.1A] | 0xFFFF
10115 | L2A | 16 unsigned int | line2 current [0.1A] | 0xFFFF
10116 | L3A | 16 unsigned int | line3 current [0.1A] | 0xFFFF
10117 | HZ | 16 unsigned int | Grid frequency | 0xFFFF
10118 | DCA1 | 16 unsigned int | DC currrent input 1 [0.1A] | 0xFFFF
10119 | DCU1 | 16 unsigned int | DC voltage input 1 [0.1V] | 0xFFFF
10120 | DCP1 | 16 signed int | DC power input 1 [0.1kW] | 0x8000
10121 | DCA2 | 16 unsigned int | DC currrent input 2 [0.1A] | 0xFFFF
10122 | DCU2 | 16 unsigned int | DC voltage input 2 [0.1V] | 0xFFFF
10123 | DCP2 | 16 signed int | DC power input 2 [0.1kW] | 0x8000
10124 | DCA3 | 16 unsigned int | DC currrent input 3 [0.1A] | 0xFFFF
10125 | DCU3 | 16 unsigned int | DC voltage input 3 [0.1V] | 0xFFFF
10126 | DCP3 | 16 signed int | DC power input 3 [0.1kW] | 0x8000
10127 | DCA4 | 16 unsigned int | DC currrent input 4 [0.1A] | 0xFFFF
10128 | DCU4 | 16 unsigned int | DC voltage input 4 [0.1V] | 0xFFFF
10129 | DCP4 | 16 signed int | DC power input 4 [0.1kW] | 0x8000
10130..10131 | WH | 32 unsigned int (byte order: ABCD) | Energy total [kWh] | 0xFFFFFFFF
10132..10133 | WH_DAY | 32 unsigned int (byte order: ABCD) | Energy current day [0.1kWh] | 0xFFFFFFFF
10134..10135 | HOURS | 32 unsigned int (byte order: ABCD) | Operation time total [hours] | 0xFFFFFFFF
10136 | MIN_DAY | 16 unsigned int | Operation time current day [minuttes] | 0xFFFF
10137 | CAB_TEMP | 16 signed int | Cabinet temperature [0.1C] | 0x8000
10138 | STATE | 16 unsigned int | Inverter state | 0xFFFF
10139..10140 | EVT1 | 32 unsigned int (byte order: ABCD) | Event field 1 | 0xFFFFFFFF
10141..10142 | EVT2 | 32 unsigned int (byte order: ABCD) | Event field 2 | 0xFFFFFFFF
10143..10144 | EVT3 | 32 unsigned int (byte order: ABCD) | Event field 3 | 0xFFFFFFFF
10145..10146 | EVT4 | 32 unsigned int (byte order: ABCD) | Event field 4 | 0xFFFFFFFF
10147..10198 | RESERVED | Not defined | Reserved for later use | Not defined
10199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Sensor number 1 to 4 The addressses of Sensor number x is found by: AddressSensor_x = (x-1) * 20 + Address
Address | DataLabel | DataType | Description | Not available value
20000 | POA | 16 unsigned int | Plane of Aray irradiance [W/m2] | 0xFFFF
20001 | BOM | 16 signed int | Back of module temperature [0.1C] | 0x8000
20002 | GHI | 16 unsigned int | Global horizontal irradiance [W/m2] | 0xFFFF
20003 | AMB_TEMP | 16 signed int | Ambient temperature [0.1C] | 0x8000
20004 | WIND_SPEED | 16 unsigned int | Wind speed [0.1m/s] | 0xFFFF
20005 | REL_HUMIDITY | 16 signed int | Relative humidity [%] | 0x8000
20006 | BAR_PRES | 16 signed int | Barometrical pressure [HPa] | 0x8000
20007 | WIND_DIR | 16 signed int | Wind direction [deg] | 0x8000
20008 | RAIN | 16 signed int | Rain fall [mm] | 0x8000
20009 | FUEL_LEVEL | 16 signed int | Fuel Level [0.1%] | 0x8000
20010 | FUEL_PRESSURE | 16 signed int | Fuel pressure [mbar] | 0x8000
20011..20018 | RESERVED | Not defined | Reserved for later use | Not defined
20019 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
IO module number 1 to 4 The addressses of module number x is found by: AddressModule_x = (x-1) * 50 + Address
Address | DataLabel | DataType | Description | Not available value
20500 | INPUT_1_16 | 16 unsigned int | bitwise | Not defined
20501 | OUTPUT_1_16 | 16 unsigned int | bitwise | Not defined
20502..20503 | AIO_INPUT_01 | FLOAT (byte order: ABCD) | Analogue input 01 | Not defined
20504..20505 | AIO_INPUT_02 | FLOAT (byte order: ABCD) | Analogue input 02 | Not defined
20506..20507 | AIO_INPUT_03 | FLOAT (byte order: ABCD) | Analogue input 03 | Not defined
20508-20509 | AIO_INPUT_04 | FLOAT (byte order: ABCD) | Analogue input 04 | Not defined
20510..20511 | AIO_INPUT_05 | FLOAT (byte order: ABCD) | Analogue input 05 | Not defined
20512..20513 | AIO_INPUT_06 | FLOAT (byte order: ABCD) | Analogue input 06 | Not defined
20514..20515 | AIO_INPUT_07 | FLOAT (byte order: ABCD) | Analogue input 07 | Not defined
20516..20517 | AIO_INPUT_08 | FLOAT (byte order: ABCD) | Analogue input 08 | Not defined
20518..20519 | AIO_OUTPUT_01 | FLOAT (byte order: ABCD) | Analogue output 01 | Not defined
20520..20521 | AIO_OUTPUT_02 | FLOAT (byte order: ABCD) | Analogue output 02 | Not defined
20522..20523 | AIO_OUTPUT_03 | FLOAT (byte order: ABCD) | Analogue output 03 | Not defined
20524..20525 | AIO_OUTPUT_04 | FLOAT (byte order: ABCD) | Analogue output 04 | Not defined
20526..20527 | AIO_OUTPUT_05 | FLOAT (byte order: ABCD) | Analogue output 05 | Not defined
20528..20529 | AIO_OUTPUT_06 | FLOAT (byte order: ABCD) | Analogue output 06 | Not defined
20530..20531 | AIO_OUTPUT_07 | FLOAT (byte order: ABCD) | Analogue output 07 | Not defined
20532..20533 | AIO_OUTPUT_08 | FLOAT (byte order: ABCD) | Analogue output 08 | Not defined
20534 | CH_CONF_01 | 16 unsigned int | Channel confirguration 01 | Not defined
20535 | CH_CONF_02 | 16 unsigned int | Channel confirguration 02 | Not defined
20536 | CH_CONF_03 | 16 unsigned int | Channel confirguration 03 | Not defined
20537 | CH_CONF_04 | 16 unsigned int | Channel confirguration 04 | Not defined
20538 | CH_CONF_05 | 16 unsigned int | Channel confirguration 05 | Not defined
20539 | CH_CONF_06 | 16 unsigned int | Channel confirguration 06 | Not defined
20540 | CH_CONF_07 | 16 unsigned int | Channel confirguration 07 | Not defined
20541 | CH_CONF_08 | 16 unsigned int | Channel confirguration 08 | Not defined
20542 | CH_STATUS | 16 unsigned int | Channel status | Not defined
20543 | MOD_TEMP | 16 unsigned int | Module temperature [0.1C] | Not defined
20544..20548 | RESERVED | Not defined | Reserved for later use | Not defined
20549 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
CONFIGURABLE MODBUS AREA
20900..20947 | CONF_MODBUS_AREA_ADDR_0_47 | Not defined | Data mapped from the rest of the starndard modbus map (fcn 0x04) | Not defined
ECLOGIC BUILDER AREA 1
28000 | Q1 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28001 | Q2 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28002 | Q3 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28003 | Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28004 | Inverted Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28005..28099 | RESERVED | Not defined | Reserved for later use | Not defined
SPOTPRICE AREA
28100 | SPOTPRICE_BIT_STATUS | 16 unsigned int | BIT0: Spotprices valid BIT1: Spotprice negative | Not defined
28101..28148 | SPOTPRICES | FLOAT (byte order: ABCD) | Todays hourly spotprices [00..23] from the selected market [Euro/MWh] | Not defined
28149..28150 | SPOTPRICE_IMPORT_CURRENCY_KWH | FLOAT (byte order: ABCD) | Instant spot price including import tariff [currency/kWh] | Not defined
28151..28152 | SPOTPRICE_EXPORT_CURRENCY_KWH | FLOAT (byte order: ABCD) | Instant spot price including export tariff [currency/kWh] | Not defined
28153..28200 | SPOTPRICE_IMPORT_TARIFF | FLOAT (byte order: ABCD) | Todays hourly import tariffs [00..23] from the selected market [currency/kWh] | Not defined
28201..28248 | SPOTPRICE_EXPORT_TARIFF | FLOAT (byte order: ABCD) | Todays hourly export tariffs [00..23] from the selected market [currency/kWh] | Not defined
28249..28499 | RESERVED | Not defined | Reserved for later use | Not defined
ECLOGIC LINKER COMMAND AREA 1
29000 | GB_POSITION 1-16 | 16 unsigned int | bitwise | Not defined
29001 | MB_POSITION 1-16 | 16 unsigned int | bitwise | Not defined
29002 | Relay 1-16 on all DG meters | 16 unsigned int | bitwise | Not defined
29003 | Relay 1-16 on DG meter 1 | 16 unsigned int | bitwise | Not defined
29004 | Relay 1-16 on DG meter 2 | 16 unsigned int | bitwise | Not defined
29005 | Relay 1-16 on DG meter 3 | 16 unsigned int | bitwise | Not defined
29006 | Relay 1-16 on DG meter 4 | 16 unsigned int | bitwise | Not defined
29007 | Relay 1-16 on DG meter 5 | 16 unsigned int | bitwise | Not defined
29008 | Relay 1-16 on DG meter 6 | 16 unsigned int | bitwise | Not defined
29009 | Relay 1-16 on DG meter 7 | 16 unsigned int | bitwise | Not defined
29010 | Relay 1-16 on DG meter 8 | 16 unsigned int | bitwise | Not defined
29011 | Relay 1-16 on DG meter 9 | 16 unsigned int | bitwise | Not defined
29012 | Relay 1-16 on DG meter 10 | 16 unsigned int | bitwise | Not defined
29013 | Relay 1-16 on DG meter 11 | 16 unsigned int | bitwise | Not defined
29014 | Relay 1-16 on DG meter 12 | 16 unsigned int | bitwise | Not defined
29015 | Relay 1-16 on DG meter 13 | 16 unsigned int | bitwise | Not defined
29016 | Relay 1-16 on DG meter 14 | 16 unsigned int | bitwise | Not defined
29017 | Relay 1-16 on DG meter 15 | 16 unsigned int | bitwise | Not defined
29018 | Relay 1-16 on DG meter 16 | 16 unsigned int | bitwise | Not defined
29019 | Relay 1-16 on all PV meters | 16 unsigned int | bitwise | Not defined
29020 | Relay 1-16 on PV meter 1 | 16 unsigned int | bitwise | Not defined
29021 | Relay 1-16 on PV meter 2 | 16 unsigned int | bitwise | Not defined
29022 | Relay 1-16 on PV meter 3 | 16 unsigned int | bitwise | Not defined
29023 | Relay 1-16 on PV meter 4 | 16 unsigned int | bitwise | Not defined
29024 | Relay 1-16 on PV meter 5 | 16 unsigned int | bitwise | Not defined
29025 | Relay 1-16 on PV meter 6 | 16 unsigned int | bitwise | Not defined
29026 | Relay 1-16 on PV meter 7 | 16 unsigned int | bitwise | Not defined
29027 | Relay 1-16 on PV meter 8 | 16 unsigned int | bitwise | Not defined
29028 | Relay 1-16 on PV meter 9 | 16 unsigned int | bitwise | Not defined
29029 | Relay 1-16 on PV meter 10 | 16 unsigned int | bitwise | Not defined
29030 | Relay 1-16 on PV meter 11 | 16 unsigned int | bitwise | Not defined
29031 | Relay 1-16 on PV meter 12 | 16 unsigned int | bitwise | Not defined
29032 | Relay 1-16 on PV meter 13 | 16 unsigned int | bitwise | Not defined
29033 | Relay 1-16 on PV meter 14 | 16 unsigned int | bitwise | Not defined
29034 | Relay 1-16 on PV meter 15 | 16 unsigned int | bitwise | Not defined
29035 | Relay 1-16 on PV meter 16 | 16 unsigned int | bitwise | Not defined
29036 | Relay 1-16 on all Mains meters | 16 unsigned int | bitwise | Not defined
29037 | Relay 1-16 on Mains meter 1 | 16 unsigned int | bitwise | Not defined
29038 | Relay 1-16 on Mains meter 2 | 16 unsigned int | bitwise | Not defined
29039 | Relay 1-16 on Mains meter 3 | 16 unsigned int | bitwise | Not defined
29040 | Relay 1-16 on Mains meter 4 | 16 unsigned int | bitwise | Not defined
29041 | Relay 1-16 on Mains meter 5 | 16 unsigned int | bitwise | Not defined
29042 | Relay 1-16 on Mains meter 6 | 16 unsigned int | bitwise | Not defined
29043 | Relay 1-16 on Mains meter 7 | 16 unsigned int | bitwise | Not defined
29044 | Relay 1-16 on Mains meter 8 | 16 unsigned int | bitwise | Not defined
29045 | Relay 1-16 on Mains meter 9 | 16 unsigned int | bitwise | Not defined
29046 | Relay 1-16 on Mains meter 10 | 16 unsigned int | bitwise | Not defined
29047 | Relay 1-16 on Mains meter 11 | 16 unsigned int | bitwise | Not defined
29048 | Relay 1-16 on Mains meter 12 | 16 unsigned int | bitwise | Not defined
29049 | Relay 1-16 on Mains meter 13 | 16 unsigned int | bitwise | Not defined
29050 | Relay 1-16 on Mains meter 14 | 16 unsigned int | bitwise | Not defined
29051 | Relay 1-16 on Mains meter 15 | 16 unsigned int | bitwise | Not defined
29052 | Relay 1-16 on Mains meter 16 | 16 unsigned int | bitwise | Not defined
29053 | Mimimum genset load 1-8 | 16 unsigned int | bitwise | Not defined
29054 | Genset1 rated power 1-8 | 16 unsigned int | bitwise | Not defined
29055 | RRCR input 1-4 | 16 unsigned int | bitwise | Not defined
29056 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise | Not defined
29057 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise | Not defined
29058 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise | Not defined
29059 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise | Not defined
29060 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise | Not defined
29061..29064 | Not used | Not used | Not used | Not defined
29065 | AIO RRCR input | 16 unsigned int | bitwise | Not defined
29066 | Cmd panel LED01..16: Green | 16 unsigned int | bitwise | Not defined
29067 | Cmd panel LED01..16: Red | 16 unsigned int | bitwise | Not defined
29068 | EClogic Alarms 01..08 | 16 unsigned int | bitwise | Not defined
29069 | EClogic Timers 01..08 | 16 unsigned int | bitwise | Not defined
29070..29075 | RESERVED | Not defined | Not used | Not defined
29076 | EClogic PV Reference Overwrite | 16 unsigned int | bitwise | Not defined
29077..29078 | RESERVED | Not defined | Not used | Not defined
29079 | Eclogic P Ctrl Mode Overwrite | 16 unsigned int | BIT0: FIXED P BIT1: FIXED P PCC | Not defined
29080 | Eclogic Q Ctrl Mode Overwrite | 16 unsigned int | BIT0: FIXED Q BIT1: FIXED Q PCC BIT2: FIXED COSPHI C BIT3: FIXED COSPHI C PCC BIT4: FIXED COSPHI I BIT5: FIXED COSPHI I PCC BIT6: SHARE PF | Not defined
29081..29084 | RESERVED | Not defined | Not used | Not defined
29085 | PV commands | 16 unsigned int | BIT0: Start PV (Control) BIT1: Stop PV (Control) BIT2: Start PV (Overwrite) BIT3: Stop PV (Overwrite) | Not defined
29086..29087 | RESERVED | Not defined | Not used | Not defined
29088 | Suppress PV ctrl. functions | 16 unsigned int | BIT0: Suppress SunSpec Slave | Not defined
29089..29999 | RESERVED | Not defined | Reserved for later use | Not defined
MISC AREA 1
Address | DataLabel | DataType | Description | Not available value
30000..30001 | POWER_P_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset active power [kW] | Not defined
30002..30003 | POWER_Q_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset reactive power [kVAr] | Not defined
30004..30005 | POWER_S_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset apperant power [kVAr] | Not defined
30006..30007 | POWER_COSPHI_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset cosphi | Not defined
30008 | IND_CAP_DG | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30009..30010 | POWER_P_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV active power [kW] | Not defined
30011..30012 | POWER_Q_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV reactive power [kVAr] | Not defined
30013..30014 | POWER_S_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV apperant power [kVAr] | Not defined
30015..30016 | POWER_COSPHI_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV cosphi | Not defined
30017 | IND_CAP_PV | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30018..30019 | POWER_P_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains active power [kW] | Not defined
30020..30021 | POWER_Q_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains reactive power [kVAr] | Not defined
30022..30023 | POWER_S_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains apperant power [kVAr] | Not defined
30024..30025 | POWER_COSPHI_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains cosphi | Not defined
30026 | IND_CAP_MAINS | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30027..30028 | POWER_P_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total active power load [kW] | Not defined
30029..30030 | POWER_Q_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total reactive power load [kVAr] | Not defined
30031..30032 | POWER_S_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total apperant power load [kVAr] | Not defined
30033..30034 | POWER_COSPHI_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total load cosphi | Not defined
30035 | IND_CAP_LOAD | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30036..30037 | DG_KWH_TOTAL | FLOAT (byte order: ABCD) | Total genset energy production [kWh] | Not defined
30038..30039 | DG_KWH_YEAR | FLOAT (byte order: ABCD) | Genset energy production current year [kWh] | Not defined
30040..30041 | DG_KWH_MONTH | FLOAT (byte order: ABCD) | Genset energy production current month [kWh] | Not defined
30042..30043 | DG_KWH_DAY | FLOAT (byte order: ABCD) | Genset energy production current day [kWh] | Not defined
30044..30045 | PV_KWH_TOTAL | FLOAT (byte order: ABCD) | Total PV energy production [kWh] | Not defined
30046..30047 | PV_KWH_YEAR | FLOAT (byte order: ABCD) | PV energy production current year [kWh] | Not defined
30048..30049 | PV_KWH_MONTH | FLOAT (byte order: ABCD) | PV energy production current month [kWh] | Not defined
30050..30051 | PV_KWH_DAY | FLOAT (byte order: ABCD) | PV energy production current day [kWh] | Not defined
30052..30053 | PV_KWH_CUR_TOTAL | FLOAT (byte order: ABCD) | Total PV energy production curtailed [kWh] | Not defined
30054..30055 | PV_KWH_CUR_YEAR | FLOAT (byte order: ABCD) | PV energy production curtailed current year [kWh] | Not defined
30056..30057 | PV_KWH_CUR_MONTH | FLOAT (byte order: ABCD) | PV energy production curtailed current month [kWh] | Not defined
30058..30059 | PV_KWH_CUR_DAY | FLOAT (byte order: ABCD) | PV energy production curtailed current day [kWh] | Not defined
30060..30061 | MAINS_KWH_TOTAL | FLOAT (byte order: ABCD) | Total energy imported from Mains [kWh] | Not defined
30062..30063 | MAINS_KWH_YEAR | FLOAT (byte order: ABCD) | Energy imported from Mains current year [kWh] | Not defined
30064..30065 | MAINS_KWH_MONTH | FLOAT (byte order: ABCD) | Energy imported from Mains current month [kWh] | Not defined
30066..30667 | MAINS_KWH_DAY | FLOAT (byte order: ABCD) | Energy imported from Mains current day [kWh] | Not defined
30068..30069 | MAINS_KWH_EXP_TOTAL | FLOAT (byte order: ABCD) | Total energy exported to Mains [kWh] | Not defined
30070..30071 | MAINS_KWH_EXP_YEAR | FLOAT (byte order: ABCD) | Energy exported to Mains current year [kWh] | Not defined
30072..30073 | MAINS_KWH_EXP_MONTH | FLOAT (byte order: ABCD) | Energy exported to Mains current month [kWh] | Not defined
30074..30075 | MAINS_KWH_EXP_DAY | FLOAT (byte order: ABCD) | Energy exported to Mains current day [kWh] | Not defined
30076…30077 | LOAD_KWH_TOTAL | FLOAT (byte order: ABCD) | Total energy consumed [kWh] | Not defined
30078..30079 | LOAD_KWH_YEAR | FLOAT (byte order: ABCD) | Energy consumed current year [kWh] | Not defined
30080..30081 | LOAD_KWH_MONTH | FLOAT (byte order: ABCD) | Energy consumed current month [kWh] | Not defined
30082..30083 | LOAD_KWH_DAY | FLOAT (byte order: ABCD) | Energy consumed current day [kWh] | Not defined
30084..30085 | PV_FUEL_SAVE_TOTAL | FLOAT (byte order: ABCD) | Fuel volume saving total [user defined, default: liter] | Not defined
30086..30087 | PV_FUEL_SAVE_YEAR | FLOAT (byte order: ABCD) | Fuel volume saving current year [user defined, default: liter] | Not defined
30088..30089 | PV_FUEL_SAVE_MONTH | FLOAT (byte order: ABCD) | Fuel volume saving current month [user defined, default: liter] | Not defined
30090..30091 | PV_FUEL_SAVE_DAY | FLOAT (byte order: ABCD) | Fuel volume saving current day [user defined, default: liter] | Not defined
30092..30093 | PV_FUEL_EXPEN_SAVE_TOTAL | FLOAT (byte order: ABCD) | Fuel expense savings total [user defined, default: euro] | Not defined
30094..30095 | PV_FUEL_EXPEN_SAVE_YEAR | FLOAT (byte order: ABCD) | Fuel expense savings current year [user defined, default: euro] | Not defined
30096..30097 | PV_FUEL_EXPEN_SAVE_MONTH | FLOAT (byte order: ABCD) | Fuel expense savings current month [user defined, default: euro] | Not defined
30098..30099 | PV_FUEL_EXPEN_SAVE_DAY | FLOAT (byte order: ABCD) | Fuel expense savings current day [user defined, default: euro] | Not defined
30100..30101 | PV_FUEL_EMISS_SAVE_TOTAL | FLOAT (byte order: ABCD) | CO2 emission savings total [user defined, default: kg] | Not defined
30102..30103 | PV_FUEL_EMISS_SAVE_YEAR | FLOAT (byte order: ABCD) | CO2 emission savings current year [user defined, default: kg] | Not defined
30104..30105 | PV_FUEL_EMISS_SAVE_MONTH | FLOAT (byte order: ABCD) | CO2 emission savings current month [user defined, default: kg] | Not defined
30106..30107 | PV_FUEL_EMISS_SAVE_DAY | FLOAT (byte order: ABCD) | CO2 emission savings current day [user defined, default: kg] | Not defined
30108..30109 | PV_EXP_SAVE_TOTAL | FLOAT (byte order: ABCD) | PV export yield total [user defined, default: euro] | Not defined
30110..30111 | PV_EXP_SAVE_YEAR | FLOAT (byte order: ABCD) | PV export yield current year [user defined, default: euro] | Not defined
30112..30113 | PV_EXP_SAVE_MONTH | FLOAT (byte order: ABCD) | PV export yield current month [user defined, default: euro] | Not defined
30114..30115 | PV_EXP_SAVE_DAY | FLOAT (byte order: ABCD) | PV export yield current day [user defined, default: euro] | Not defined
30116..30117 | MAINS_IMP_SAVE_TOTAL | FLOAT (byte order: ABCD) | Mains import expense savings total [user defined, default: euro] | Not defined
30118..30119 | MAINS_IMP_SAVE_YEAR | FLOAT (byte order: ABCD) | Mains import expense savings current year [user defined, default: euro] | Not defined
30120..30121 | MAINS_IMP_SAVE_MONTH | FLOAT (byte order: ABCD) | Mains import expense savings current month [user defined, default: euro] | Not defined
30122..30123 | MAINS_IMP_SAVE_DAY | FLOAT (byte order: ABCD) | Mains import expense savings current day [user defined, default: euro] | Not defined
30124..30125 | DG_FUEL_CON_TOTAL | FLOAT (byte order: ABCD) | Fuel volume consumed total [user defined, default: liter] | Not defined
30126..30127 | DG_FUEL_CON_YEAR | FLOAT (byte order: ABCD) | Fuel volume consumed current year [user defined, default: liter] | Not defined
30128..30129 | DG_FUEL_CON_MONTH | FLOAT (byte order: ABCD) | Fuel volume consumed current month [user defined, default: liter] | Not defined
30130..30131 | DG_FUEL_CON_DAY | FLOAT (byte order: ABCD) | Fuel volume consumed current day [user defined, default: liter] | Not defined
30132..30133 | DG_FUEL_EXPEN_CON_TOTAL | FLOAT (byte order: ABCD) | Fuel expense total [user defined, default: euro] | Not defined
30134..30135 | DG_FUEL_EXPEN_CON_YEAR | FLOAT (byte order: ABCD) | Fuel expense current year [user defined, default: euro] | Not defined
30136..30137 | DG_FUEL_EXPEN_CON_MONTH | FLOAT (byte order: ABCD) | Fuel expense current month [user defined, default: euro] | Not defined
30138..30139 | DG_FUEL_EXPEN_CON_DAY | FLOAT (byte order: ABCD) | Fuel expense current day [user defined, default: euro] | Not defined
30140..30141 | DG_FUEL_EMISS_CON_TOTAL | FLOAT (byte order: ABCD) | CO2 emission total [user defined, default: kg] | Not defined
30142..30143 | DG_FUEL_EMISS_CON_YEAR | FLOAT (byte order: ABCD) | CO2 emission current year [user defined, default: kg] | Not defined
30144..30145 | DG_FUEL_EMISS_CON_MONTH | FLOAT (byte order: ABCD) | CO2 emission current month [user defined, default: kg] | Not defined
30146..30147 | DG_FUEL_EMISS_CON_DAY | FLOAT (byte order: ABCD) | CO2 emission current day [user defined, default: kg] | Not defined
30148..30149 | MAINS_IMP_CON_TOTAL | FLOAT (byte order: ABCD) | Mains import expense total [user defined, default: euro] | Not defined
30150..30151 | MAINS_IMP_CON_YEAR | FLOAT (byte order: ABCD) | Mains import expense current year [user defined, default: euro] | Not defined
30152..30153 | MAINS_IMP_CON_MONTH | FLOAT (byte order: ABCD) | Mains import expense current month [user defined, default: euro] | Not defined
30154..30155 | MAINS_IMP_CON_DAY | FLOAT (byte order: ABCD) | Mains import expense current day [user defined, default: euro] | Not defined
30156..30157 | MAINS_EXP_SAVE_TOTAL | FLOAT (byte order: ABCD) | Mains export yield total [user defined, default: euro] | Not defined
30158..30159 | MAINS_EXP_SAVE_YEAR | FLOAT (byte order: ABCD) | Mains export yield current year [user defined, default: euro] | Not defined
30160..30161 | MAINS_EXP_SAVE_MONTH | FLOAT (byte order: ABCD) | Mains export yield current month [user defined, default: euro] | Not defined
30162..30163 | MAINS_EXP_SAVE_DAY | FLOAT (byte order: ABCD) | Mains export yield current day [user defined, default: euro] | Not defined
30164..30165 | PV_PENETRATION_TOTAL | FLOAT (byte order: ABCD) | PV penetration ratio total [%] | Not defined
30166..30167 | PV_PENETRATION_YEAR | FLOAT (byte order: ABCD) | PV penetration ratio current year [%] | Not defined
30168..30169 | PV_PENETRATION_MONTH | FLOAT (byte order: ABCD) | PV penetration ratio current month [%] | Not defined
30170..30171 | PV_PENETRATION_DAY | FLOAT (byte order: ABCD) | PV penetration ratio current day [%] | Not defined
30172..30173 | PV_PERFORMANCE_TOTAL | FLOAT (byte order: ABCD) | PV performance ratio total [%] | Not defined
30174..30175 | PV_PERFORMANCE_YEAR | FLOAT (byte order: ABCD) | PV performance ratio current year [%] | Not defined
30176..30177 | PV_PERFORMANCE_MONTH | FLOAT (byte order: ABCD) | PV performance ratio current month [%] | Not defined
30178..30179 | PV_PERFORMANCE_DAY | FLOAT (byte order: ABCD) | PV performance ratio current day [%] | Not defined
Genset 1 to 16 The addressses of genset number x is found by: Address_x = (x-1) * 2 + Address
30180..30181 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30212..30213 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
PV 1 to 16 The addressses of PV number x is found by: Address_x = (x-1) * 2 + Address
30244..30245 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30276..30277 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
Mains 1 to 16 The addressses of Mains number x is found by: Address_x = (x-1) * 2 + Address
30308..30309 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30340..30341 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
Inverter 1 to 32 The addressses of inverter number x is found by: Address_x = (x-1) * 2 + Address
30372..30373 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30436..30437 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
MISC AREA 2
30500..30501 | SENSOR_POA | FLOAT (byte order: ABCD) | POA irradiance [W/m2] | Not defined
30502..30503 | SENSOR_BOM | FLOAT (byte order: ABCD) | Back of module temperature [C] | Not defined
30504..30505 | PV_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total PV generating capacity active power [kW] | Not defined
30506..30507 | PV_Q_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total PV generating capacity reactive power [kVAr] | Not defined
30508..30509 | DG_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total genset generating capacity active power [kW] | Not defined
30510..30511 | DG_P_LOADING_PCT | FLOAT (byte order: ABCD) | Genset active power loading [%] | Not defined
30512..30513 | DG_P_MIN_LOADING_KW | FLOAT (byte order: ABCD) | Minimum genset load [kW] | Not defined
30514..30515 | PV_P_POWER_TARGET | FLOAT (byte order: ABCD) | PV target reference active power [kW] | Not defined
30516..30517 | PV_P_POWER_REFERENCE | FLOAT (byte order: ABCD) | PV actual reference active power [kW] | Not defined
30518..30519 | PV_Q_POWER_TARGET | FLOAT (byte order: ABCD) | PV target reference reactive power [kVAr] | Not defined
30520..30521 | PV_Q_POWER_REFERENCE | FLOAT (byte order: ABCD) | PV actual reference reactive power [kVAr] | Not defined
30522..30523 | MAINS_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Mains generating capacity active power [kW] | Not defined
30524..30525 | P_PV_LOAD_PCT | FLOAT (byte order: ABCD) | PV active power loading [%] | Not defined
30526..30527 | Q_PV_LOAD_PCT | FLOAT (byte order: ABCD) | PV reactive power loading [%] | Not defined
30528..30529 | Q_DG_LOAD_PCT | FLOAT (byte order: ABCD) | Genset reactive power loading [%] | Not defined
30530..30531 | P_MAINS_LOAD_PCT | FLOAT (byte order: ABCD) | Mains active power loading [%] | Not defined
30532..30533 | Q_MAINS_LOAD_PCT | FLOAT (byte order: ABCD) | Mains reactive power loading [%] | Not defined
30534..30535 | P_PV_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | PV active power error in regards to refernce [%] | Not defined
30536..30537 | Q_PV_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | PV reactive power error in regards to refernce [%] | Not defined
30538..30539 | P_DG_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Genset active power error in regards to refernce [%] | Not defined
30540..30541 | Q_DG_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Genset reactive power error in regards to refernce [%] | Not defined
30542..30543 | P_MAINS_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Mains active power error in regards to refernce [%] | Not defined
30544..30545 | Q_MAINS_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Mains reactive power error in regards to refernce [%] | Not defined
30546..30547 | LATITUDE | FLOAT (byte order: ABCD) | Latitude GPS coordinate | Not defined
30548..30549 | LONGITUDE | FLOAT (byte order: ABCD) | Longitude GPS coordinate | Not defined
30550..30551 | SENSOR_GHI | FLOAT (byte order: ABCD) | GHI irradiance [W/m2] | Not defined
30552..30553 | SENSOR_AMBIENT_TEMP | FLOAT (byte order: ABCD) | Ambient temperature [C] | Not defined
30554..30555 | SENSOR_WIND_SPEED | FLOAT (byte order: ABCD) | Wind speed [m/s] | Not defined
30556..30557 | SENSOR_REL_HUMIDITY | FLOAT (byte order: ABCD) | Relative humidity [%] | Not defined
30558..30559 | SENSOR_BAR_PRES | FLOAT (byte order: ABCD) | Barometrical pressure [HPa] | Not defined
30560..30561 | SENSOR_WIND_DIR | FLOAT (byte order: ABCD) | Wind direction [deg] | Not defined
30562..30563 | SENSOR_RAIN | FLOAT (byte order: ABCD) | Rain fall [mm] | Not defined
30564..30565 | POWER_P_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset active power [kW] | Not defined
30566..30567 | POWER_Q_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset reactive power [kVAr] | Not defined
30568..30569 | POWER_P_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV active power [kW] | Not defined
30570..30571 | POWER_Q_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV reactive power [kVAr] | Not defined
30572..30573 | POWER_P_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total mains active power [kW] | Not defined
30574..30575 | POWER_Q_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total mains reactive power [kVAr] | Not defined
30576..30577 | POWER_P_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total load active power [kW] | Not defined
30578..30579 | POWER_Q_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total load reactive power [kVAr] | Not defined
30580..30581 | POWER_P_PV_CURTAILED | FLOAT (byte order: ABCD) | Total active power being curtailed [kW] | Not defined
30582..30583 | PV_KWH_AVA_TOTAL | FLOAT (byte order: ABCD) | Total PV energy available [kWh] | Not defined
30584..30585 | PV_KWH_AVA_YEAR | FLOAT (byte order: ABCD) | PV energy available current year [kWh] | Not defined
30586..30587 | PV_KWH_AVA_MONTH | FLOAT (byte order: ABCD) | PV energy available current month [kWh] | Not defined
30588..30589 | PV_KWH_AVA_DAY | FLOAT (byte order: ABCD) | PV energy available current day [kWh] | Not defined
30590..30591 | FUEL_LEVEL_01 | FLOAT (byte order: ABCD) | Fuel level 01 [%] | Not defined
30592..30593 | FUEL_LEVEL_02 | FLOAT (byte order: ABCD) | Fuel level 02 [%] | Not defined
30594..30595 | FUEL_LEVEL_03 | FLOAT (byte order: ABCD) | Fuel level 03 [%] | Not defined
30596..30597 | FUEL_LEVEL_04 | FLOAT (byte order: ABCD) | Fuel level 04 [%] | Not defined
30598..30599 | FUEL_PRESS_01 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30600..30601 | FUEL_PRESS_02 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30602..30603 | FUEL_PRESS_03 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30604..30605 | FUEL_PRESS_04 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30606..30827 | Reserved | Not defined | Reserved for later use | Not defined
30828..30829 | PV_P_POWER_REFERENCE_PCT | FLOAT (byte order: ABCD) | PV actual reference active power [%] | Not defined
30830..30831 | PV_Q_POWER_REFERENCE_PCT | FLOAT (byte order: ABCD) | PV actual reference reactive power [%] | Not defined
30832..30994 | Reserved | Not defined | Reserved for later use | Not defined
30995..30996 | POWER_P_DG_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total genset acive power plus grid active power [kW] | Not defined
30997..30998 | POWER_Q_DG_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total genset acive power plus grid reactive power [kW] | Not defined
30999 | ECPV_SW_VERSION | 16 unsigned int | SW version opf the ECpv application SW
BITFIELD AREA 1
31000 | BITFIELD_1 | 16 unsigned int | GB ON 1..16 | Not defined
31001 | BITFIELD_2 | 16 unsigned int | MB ON 1..16 | Not defined
31002 | BITFIELD_3 | 16 unsigned int | BIT0: Any GB ON BIT1: Any MB ON BIT2: Curtailment active BIT3: PV started BIT4: PV stopped BIT5: Genset management: DG started BIT6: Genset management: DG stopped BIT7: Simulation: Active BIT8: Night time: Active BIT9: Show ECpanel password in clear text | Not defined
31003 | BITFIELD_4 | 16 unsigned int | BIT0: Any inverter missing BIT1: Inverter socket connection alarm BIT2: Any genset meter missing BIT3: Genset meter socket connection alarm BIT4: Any PV meter missing BIT5: PV meter socket connection alarm BIT6: Any Mains meter missing BIT7: Mains meter socket connection alarm BIT8: Sensor 1 missing BIT9: Sensor 2 missing BIT10: Sensor 3 missing BIT11: Sensor 4 missing BIT12: SunSpec incompatible BIT13: COM2 slave timeout BIT14: COM3 slave timeout BIT15: TCP slave timeout | Not defined
31004 | BITFIELD_5 | 16 unsigned int | BIT0: Event log FTP fail BIT1: Production log FTP fail BIT2: Summary log FTP fail BIT3: Test FTP fail BIT4: Event log mail fail BIT5: Production log mail fail BIT6: Summary log mail fail BIT7: Test mail fail | Not defined
31005 | BITFIELD_6 | 16 unsigned int | BIT0: Genset low power alarm BIT1: Mains low power alarm BIT2: DG management: Genset start failure alarm BIT3: DG management: Genset stop failure alarm BIT4: COM2 modbus slave timeout BIT5: COM3 modbus slave timeout BIT6: TCP modbus slave timeout BIT7: Reserved BIT8: Reserved BIT9: Fuel level alarm BIT10: Common modbus master comm. alarm | Not defined
31006 | BITFIELD_7 | 16 unsigned int | Inverter 01-16 missing | Not defined
31007 | BITFIELD_8 | 16 unsigned int | Inverter 17-32 missing | Not defined
31008 | BITFIELD_9 | 16 unsigned int | DG meter 01-16 missing | Not defined
31009 | BITFIELD_10 | 16 unsigned int | PV meter 01-16 missing | Not defined
31010 | BITFIELD_11 | 16 unsigned int | Mains meter 01-16 missing | Not defined
31011 | BITFIELD_12 | 16 unsigned int | DG Management start commands 01-16 | Not defined
31012 | BITFIELD_13 | 16 unsigned int | DG power detected 01-16 | Not defined
31013 | BITFIELD_14 | 16 unsigned int | BIT0: IO module 1 missing BIT1: IO module 2 missing BIT2: IO module 3 missing BIT3: IO module 4 missing | Not defined
31014 | BITFIELD_15 | 16 unsigned int | EClogic Threshold output 01..16 | Not defined
31018 | BITFIELD_19 | 16 unsigned int | BIT0: EClogic Command timer 01 active BIT1: EClogic Command timer 02 active BIT2: EClogic Command timer 03 active BIT3: EClogic Command timer 04 active | Not defined
31019 | BITFIELD_20 | 16 unsigned int | Command Panel buttons 01..16 | Not defined
31020 | BITFIELD_21 | 16 unsigned int | EClogic Timers elapsed 01..16 | Not defined
31021 | BITFIELD_22 | 16 unsigned int | EClogic Modbus Event 01..16 | Not defined
31022 | BITFIELD_23 | 16 unsigned int | EClogic Modbus Event 17..32 | Not defined
31023 | BITFIELD_24 | 16 unsigned int | BIT0: EClogic alarm 01 active BIT1:EClogic alarm 02 active BIT2: EClogic alarm 03 active BIT3: EClogic alarm 04 active BIT4: EClogic alarm 05 active BIT5:EClogic alarm 06 active BIT6: EClogic alarm 07 active BIT7: EClogic alarm 08 active | Not defined
31024 | BITFIELD_25 | 16 unsigned int | ECapi Command 01..16 | Not defined
31025 | BITFIELD_26 | 16 unsigned int | ECapi Command 17..32 | Not defined
SETTINGS AREA
31700 | NBR_INVERTERS | 16 unsigned int | Number of inverters | Not defined
31701 | NBR_DG_METERS | 16 unsigned int | Number of genset meters | Not defined
31702 | NBR_PV_METERS | 16 unsigned int | Number of PV meters | Not defined
31703 | NBR_MAINS_METERS | 16 unsigned int | Number of mains meters | Not defined
31704 | SENSORS_ENABLED | 16 unsigned int | Bitwise 0: POA 1: BOM 2: GHI 3: Ambient temp. 4: Wind speed 5: Relative humidity 6: Bar pressure 7: Wind direction 8: Rain 9: Fuel level 01 10: Fuel level 02 11: Fuel level 03 12: Fuel level 04 14: Mains present 15: Genset present | Not defined
31705..31706 | INSTALLED_P_CAPACITY | FLOAT (byte order: ABCD) | installed panel capacity in kW | Not defined
31707 | INVERTER_PROTOCOL_SELECTED | 16 unsigned int | Inverter protocol selected | Not defined
31708 | DG_METER_PROTOCOL_SELECTED | 16 unsigned int | Genset meter protocol selected | Not defined
31709 | PV_METER_PROTOCOL_SELECTED | 16 unsigned int | PV meter protocol selected | Not defined
31710 | MAINS_METER_PROTOCOL_SELECTED | 16 unsigned int | Mains meter protocol selected | Not defined
31711..31715 | CURRENCY | string | Currency | Not defined
31716..31720 | VOLUME | string | Volume | Not defined
31721..31725 | MASS | string | Mass | Not defined
31726 | PV_CONTROL | Enum | PV control enabled 0: DISABLED 1: ENABLED 2: P ONLY | Not defined
31727 | GENSET_MANAGEMENT | Enum | Genset management enabled 0: DISABLED 1: NON SYNC 2: SYNC SR | Not defined
31728 | SUNSPEC_SLAVE | Enum | SunSpec slave enabled 0: DISABLED 1: ENABLED | Not defined
31729 | PROPRIERATY_SLAVE | Enum | Proprietary slave enabled 0: DISABLED 1: ENABLED | Not defined
31730 | IOS_ENABLED | 16 unsigned int | Bitwise 0: IO module 1 1: IO module 2 2: IO module 3 3: IO module 4 | Not defined
31731/31732 | INSTALLED_S_CAPACITY | FLOAT (byte order: ABCD) | installed inverter capacity in kVA | Not defined
31733/31734 | INSTALLED_Q_CAPACITY | FLOAT (byte order: ABCD) | installed inverter capacity in kVAr | Not defined
31735 | PV_CONTROL_SEC | Enum | PV secondary control enabled 0: DISABLED 1: ENABLED 2: P ONLY | Not defined
31736 | NUMBER_LGR_DG_METERS | 16 unsigned int | Number of Load meters in DG range. | Not defined
31737 | NUMBER_LGR_PV_METERS | 16 unsigned int | Number of Load meters in PV range. | Not defined
31738 | NUMBER_LGR_MAINS_METERS | 16 unsigned int | Number of Load meters in Mains range. | Not defined
31739 | SENSORS_02_ENABLED | 16 unsigned int | Bitwise 0: Fuel pressure 01 1: Fuel pressure 02 2: Fuel pressure 03 3: Fuel pressure 04 | Not defined
RTC CLOCK
32000 | Year | 16 unsigned int | ECpv RTC year | Not defined
32001 | Month | 16 unsigned int | ECpv RTC month | Not defined
32002 | Date | 16 unsigned int | ECpv RTC date | Not defined
32003 | Hour | 16 unsigned int | ECpv RTC hour | Not defined
32004 | Minute | 16 unsigned int | ECpv RTC minute | Not defined
32005 | Second | 16 unsigned int | ECpv RTC second | Not defined
32006 | Millisecond | 16 unsigned int | ECpv RTC millisecond | Not defined
IO MODULE INFO
32010 | IO_TYPE_01 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32011 | IO_TYPE_02 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32012 | IO_TYPE_03 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32013 | IO_TYPE_04 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32014 | IO_ANALOGUE_TYPE_SELECTED | 16 unsigned int | BIT0: Module 1 is analogue type BIT1: Module 2 is analogue type BIT2: Module 3 is analogue type BIT3: Module 4 is analogue type
32020..32039 | INFOTEXT_MODULE_01 | string | Info text for Module 1 type | Not defined
32040..32059 | INFOTEXT_MODULE_02 | string | Info text for Module 2 type | Not defined
32060..32079 | INFOTEXT_MODULE_03 | string | Info text for Module 3 type | Not defined
32080..32099 | INFOTEXT_MODULE_04 | string | Info text for Module 4 type | Not defined
INFO&MODE TEXT
32300 | TOTAL_DG_LOAD_METERS | 16 unsigned int | Total number of DG and load meters | Not defined
32301 | TOTAL_PV_LOAD_METERS | 16 unsigned int | Total number of PV and load meters | Not defined
32302 | TOTAL_MAINS_LOAD_METERS | 16 unsigned int | Total number of Mains and load meters | Not defined
32303 | NBR_TOT_INV_SEC_INV | 16 unsigned int | LowByte: Total number of inverter highByte: Number of secondary inverters | Not defined
32304 | INV_PROT_PRIM_SEC | 16 unsigned int | LowByte: Primary inverter protocol highByte: Secondary inverter protocol | Not defined
STAUS TEXTS
32400..32479 | STATUS_TEXT_01 | string | Status text in line 1 | Not defined
32480..32559 | STATUS_TEXT_02 | string | Status text in line 2 | Not defined
32560..32639 | STATUS_TEXT_03 | string | Status text in line 3 | Not defined
32640 | STATUS_TEXT_01_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32641 | STATUS_TEXT_02_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32642 | STATUS_TEXT_03_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32643 | NBR_OF_STATUS_TEXTS | 16 unsigned int | Number of status texts displayed | Not defined
32644 | MIN_SLIDER | 16 signed int | Minimum possible status text slider value | Not defined

## Holding Register 0x03
Proprietary profile
Address | DataLabel | DataType | Description | Note
Page01 (Settings) |  |  |  | Page01 need to be enabled
0 | Reserved
1 | Mains P control mode | enum16 | 0: FIXED P 1: FIXED P PCC
2..3 | Mains P reference | FLOAT (byteorder: ABCD) | Active power reference in kW when parallel to grid
4 | Mains Q control mode | enum16 | 0: FIXED Q 1: FIXED Q PCC 2: FIXED COSPHI C 3: FIXED COSPHI C PCC 4: FIXED COSPHI I 5: FIXED COSPHI I PCC
5..6 | Mains Q reference | FLOAT (byteorder: ABCD) | Reactive power reference in kVAr when parallel to grid and a Q ctrl method selected
7..8 | Mains cosphi reference | FLOAT (byteorder: ABCD) | Cosphi reference when parallel to grid and a cosphi ctrl method selected
9..10 | Minimum genset load | FLOAT (byteorder: ABCD) | Minimum genset operating load in percentage
11 | Genset Q control mode | enum16 | 0: ALL Q 1: SHARING Q 2: SAME COSPHI 3: FIXED COSPHI C DG 4: FIXED COSPHI I DG
12..13 | DG cosphi cap reference | FLOAT (byteorder: ABCD) | Cap cosphi reference when parallel to genset and "FIXED COSPHI C DG" selected
14..15 | DG cosphi ind reference | FLOAT (byteorder: ABCD) | Ind cosphi reference when parallel to genset and "FIXED COSPHI I DG" selected
16..17 | PV P Ramp up | FLOAT (byteorder: ABCD) | PV power ramp up rate [%/s]
18..19 | PV P Ramp down | FLOAT (byteorder: ABCD) | PV power ramp down rate [%/s]
20..21 | PV Q Ramp up | FLOAT (byteorder: ABCD) | PV reactive power ramp up rate [%/s]
22..23 | PV Q Ramp down | FLOAT (byteorder: ABCD) | PV reactive power ramp down rate [%/s]
24..25 | PV Mains Parallel P Ramp up | FLOAT (byteorder: ABCD) | PV power ramp up rate [%/s] when parallel to grid
26..27 | PV Mains Parallel P Ramp down | FLOAT (byteorder: ABCD) | PV power ramp down rate [%/s] when parallel to grid
28..29 | PV Mains Parallel Q Ramp up | FLOAT (byteorder: ABCD) | PV reactive power ramp up rate [%/s] when parallel to grid
30..31 | PV Mains Parallel Q Ramp down | FLOAT (byteorder: ABCD) | PV reactive power ramp down rate [%/s] when parallel to grid
32..63 | DG 01..16 Rated power | FLOAT (byteorder: ABCD) | Rated power of genset 01..16
64..499 | Reserved
500..501 | Sim P load | FLOAT (byteorder: ABCD) | Simulated active load
502..503 | Sim Q load | FLOAT (byteorder: ABCD) | Simulated reactive load
504..505 | Sim F grid | FLOAT (byteorder: ABCD) | Simulated grid frequency
506..507 | Sim U grid | FLOAT (byteorder: ABCD) | Simulated grid voltage
508..509 | Sim POA | FLOAT (byteorder: ABCD) | Simulated plane of array irradiation
510..511 | Sim BOM | FLOAT (byteorder: ABCD) | Simulated back of module temperature
512 | Sim MB on | 16 unsigned int | BIT0..BIT15: Mains breaker 01..16 closed
513 | Sim GB on | 16 unsigned int | BIT0..BIT15: Genset breaker 01..16 closed
514..999 | Reserved
Page02 (Commands) |  |  |  | Page02 need to be enabled
1000 | PV Start | enum16 | 0: OFF 1: ON
1001 | Genset Start | enum16 | 0: OFF 1: ON
1002 | Ack. All alarms. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1003 | Ack. All alarm in line 01. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1004 | Ack. All alarm in line 02. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1005 | Ack. All alarm in line 03. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1006 | Alarm slider | 16 signed int |  | Alarm slider control
1007 | Year | 16 unsigned int | Set ECpv RTC year
1008 | Month | 16 unsigned int | Set ECpv RTC month
1009 | Date | 16 unsigned int | Set ECpv RTC date
1010 | Hour | 16 unsigned int | Set ECpv RTC hour
1011 | Minute | 16 unsigned int | Set ECpv RTC minute
1012 | Second | 16 unsigned int | Set ECpv RTC second
1013 | Millisecond | 16 unsigned int | Set ECpv RTC millisecond
1014 | Set Ecpv RTC | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1015..1021 | Reserved
1022 | REF Enables | enum16 | BIT0: PV PREF Enable (0: OFF, 1: ON) BIT1: PV QREF Enable (0: OFF, 1: ON)
1023..1024 | PV PREF | FLOAT (byteorder: ABCD) | PV Active power reference setting used when grid connected [kW]
1025..1026 | PV QREF | FLOAT (byteorder: ABCD) | PV Reactive power reference setting used when grid connected [kVAr]
1015..1999 | Reserved
Page03 (External readings) |  |  |  | Page03 need to be enabled
2000..2001 | PV generating capacity | FLOAT (byteorder: ABCD) | PV generating panel capacity [kW] | Only used if GC compensation set to "Modbus page03".
2002..2003 | PV produced power | FLOAT (byteorder: ABCD) | The produced PV power [kW] | Only used if "Modbus page03" is selected for PV kW sensing method
2004..2005 | PV produced reactive power | FLOAT (byteorder: ABCD) | The produced PV reactive power [kVAr] | Only used if "Modbus page03" is selected for PV kW sensing method
2006..2007 | Genset generating capacity | FLOAT (byteorder: ABCD) | Gensets generating capacity connected [kW] | Only used in case "Modbus page03" is selected for GB feedback detection
2008..2009 | Genset produced power | FLOAT (byteorder: ABCD) | The total produced power of gensets connected [kW] | Only used if "Modbus page03" is selected for genset kW sensing method
2010..2011 | Genset produced reactive power | FLOAT (byteorder: ABCD) | The total produced reactive power of gensets connected [kVAr] | Only used if "Modbus page03" is selected for genset kW sensing method
2012..2013 | Grid rated capacity | FLOAT (byteorder: ABCD) | Grid rated capacity connected [kW] | Only used in case "Modbus page03" is selected for MB feedback detection
2014..2015 | Grid power | FLOAT (byteorder: ABCD) | The total grid power [kW] | Only used if "Modbus page03" is selected for mains kW sensing method
2016..2017 | Grid reactive power | FLOAT (byteorder: ABCD) | The total grid reactive power [kVAr] | Only used if "Modbus page03" is selected for mains kW sensing method
2018..2019 | Grid frequency | FLOAT (byteorder: ABCD) | The grid frequency [Hz] | Only used if "Modbus page03" is selected for mains kW sensing method
2020..2021 | Grid line-line voltage | FLOAT (byteorder: ABCD) | The grid line-line voltage [V] | Only used if "Modbus page03" is selected for mains kW sensing method
2022 | Any GB connected | 16 unsigned int | False: 0 True: 1 | Only used in case "Modbus page03" is selected for GB feedback detection
2023 | Any MB connected | 16 unsigned int | False: 0 True: 1 | Only used in case "Modbus page03" is selected for MB feedback detection
2024..2025 | POA | FLOAT (byteorder: ABCD) | POA irradiance [W/m2] | Only used in case "Modbus page03" is selected for POA Origin
2026..2027 | BOM | FLOAT (byteorder: ABCD) | Back of module temperature [C] | Only used in case "Modbus page03" is selected for BOM Origin
2028..2029 | GHI | FLOAT (byteorder: ABCD) | GHI irradiance [W/m2] | Only used in case "Modbus page03" is selected for GHI Origin
2030..2031 | Ambient temperature | FLOAT (byteorder: ABCD) | Ambient temperature [C] | Only used in case "Modbus page03" is selected for Ambient temperature Origin
2032..2033 | Wind speed | FLOAT (byteorder: ABCD) | Wind speed [m/s] | Only used in case "Modbus page03" is selected for Wind speed Origin
2034..2035 | Relative humidity | FLOAT (byteorder: ABCD) | Relative humidity [%] | Only used in case "Modbus page03" is selected for Relative humidity Origin
2036..2037 | Barometrical pressure | FLOAT (byteorder: ABCD) | Barometrical pressure [HPa] | Only used in case "Modbus page03" is selected for Barometricl pressure Origin
2038..2039 | Wind direction | FLOAT (byteorder: ABCD) | Wind direction [deg] | Only used in case "Modbus page03" is selected for Wind direction Origin
2040..2041 | Rain | FLOAT (byteorder: ABCD) | Rain fall [mm] | Only used in case "Modbus page03" is selected for Rain Origin
2042..2043 | Fuel Level 01 | FLOAT (byteorder: ABCD) | Fuel level 01 [0.1%] | Only used in case "Modbus page03" is selected for Fuel Level 01 Origin
2044..2045 | Fuel Level 02 | FLOAT (byteorder: ABCD) | Fuel level 02 [0.1%] | Only used in case "Modbus page03" is selected for Fuel level 02 Origin
2046..2047 | Fuel Level 03 | FLOAT (byteorder: ABCD) | Fuel level 03 [0.1%] | Only used in case "Modbus page03" is selected for Fuel level 03 Origin
2048..2049 | Fuel Level 04 | FLOAT (byteorder: ABCD) | Fuel level 04 [0.1%] | Only used in case "Modbus page03" is selected for Fuel level 04 Origin
2050..2999 | Reserved | FLOAT (byteorder: ABCD)
Page04 (Relay control) |  |  |  | Page04 needs to be enabled
3000 | Relay 1-16 on all DG meters | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3001 | Relay 1-16 on DG meter 1 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3002 | Relay 1-16 on DG meter 2 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3003 | Relay 1-16 on DG meter 3 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3004 | Relay 1-16 on DG meter 4 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3005 | Relay 1-16 on DG meter 5 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3006 | Relay 1-16 on DG meter 6 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3007 | Relay 1-16 on DG meter 7 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3008 | Relay 1-16 on DG meter 8 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3009 | Relay 1-16 on DG meter 9 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3010 | Relay 1-16 on DG meter 10 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3011 | Relay 1-16 on DG meter 11 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3012 | Relay 1-16 on DG meter 12 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3013 | Relay 1-16 on DG meter 13 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3014 | Relay 1-16 on DG meter 14 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3015 | Relay 1-16 on DG meter 15 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3016 | Relay 1-16 on DG meter 16 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3017 | Relay 1-16 on all PV meters | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3018 | Relay 1-16 on PV meter 1 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3019 | Relay 1-16 on PV meter 2 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3020 | Relay 1-16 on PV meter 3 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3021 | Relay 1-16 on PV meter 4 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3022 | Relay 1-16 on PV meter 5 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3023 | Relay 1-16 on PV meter 6 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3024 | Relay 1-16 on PV meter 7 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3025 | Relay 1-16 on PV meter 8 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3026 | Relay 1-16 on PV meter 9 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3027 | Relay 1-16 on PV meter 10 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3028 | Relay 1-16 on PV meter 11 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3029 | Relay 1-16 on PV meter 12 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3030 | Relay 1-16 on PV meter 13 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3031 | Relay 1-16 on PV meter 14 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3032 | Relay 1-16 on PV meter 15 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3033 | Relay 1-16 on PV meter 16 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3034 | Relay 1-16 on all Mains meters | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3035 | Relay 1-16 on Mains meter 1 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3036 | Relay 1-16 on Mains meter 2 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3037 | Relay 1-16 on Mains meter 3 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3038 | Relay 1-16 on Mains meter 4 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3039 | Relay 1-16 on Mains meter 5 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3040 | Relay 1-16 on Mains meter 6 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3041 | Relay 1-16 on Mains meter 7 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3042 | Relay 1-16 on Mains meter 8 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3043 | Relay 1-16 on Mains meter 9 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3044 | Relay 1-16 on Mains meter 10 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3045 | Relay 1-16 on Mains meter 11 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3046 | Relay 1-16 on Mains meter 12 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3047 | Relay 1-16 on Mains meter 13 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3048 | Relay 1-16 on Mains meter 14 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3049 | Relay 1-16 on Mains meter 15 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3050 | Relay 1-16 on Mains meter 16 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3051 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise
3052 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise
3053 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise
3054 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise
3055 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise
3056 | EClogic Modbus Event 01-16 | 16 unsigned int | bitwise | Maps to input register page for use in Eclogic
3057 | EClogic Modbus Event 17-32 | 16 unsigned int | bitwise | Maps to input register page for use in Eclogic
3058..3999 | Reserved
Page05 (DNP3 control) |  |  |  | Page05 needs to be enabled
4000..4001 | PV active Power [W] | FLOAT (byteorder: ABCD) | PV active power generated in Watts
4002..4003 | PV reactive Power [VAr] | FLOAT (byteorder: ABCD) | PV reactive power generated in Vars
4004..4005 | Mains active Power [W] | FLOAT (byteorder: ABCD) | Active power import/export from the grid in Watts
4006..4007 | Power reference [%] | FLOAT (byteorder: ABCD) | Active PV power reference in percentage (read)
4008..4009 | Power ramp up rate [%/min] | FLOAT (byteorder: ABCD) | Active PV power ramp up rate in %/min (read)
4010..4011 | Power ramp down rate [%/min] | FLOAT (byteorder: ABCD) | Active PV power ramp down rate in %/min (read)
4012 | Power reference [%] | 16 signed int | Active PV power reference in percentage (write)
4013 | Power ramp up rate [%/min] | 16 signed int | Active PV power ramp up rate in %/min (write)
4014 | Power ramp down rate [%/min] | 16 signed int | Active PV power ramp down rate in %/min (write)
4015..4999 | Reserved
SunSpec profile
Address | DataLabel | DataType | Description | Supported
40000..40001 | SID | 32 unsigned int | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map | x
40002 | ID | 16 unsigned int | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | x
40003 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 66 | x
40004..40019 | Manufacturer | string | Manufacturer specific value (32 chars) | x
40020..40035 | Model | string | Manufacturer specific value (32 chars) | x
40036..40043 | Options | string | Manufacturer specific value (16 chars)
40044..40051 | Version | string | Manufacturer specific value (16 chars) | x
40052..40067 | Serial Number | string | Manufacturer specific value (32 chars) | x
40068 | Device Address | 16 unsigned int | Modbus device address
40069 | Pad | 16 unsigned int | Force even alignment
40070 | ID | 16 unsigned int | A well-known value 113. Uniquely identifies this as a SunSpec Inverter (Three Phase) FLOAT Model | x
40071 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 60 | x
40072..40073 | Amps | FLOAT (byteorder: ABCD) | AC Current
40074..40075 | Amps PhaseA | FLOAT (byteorder: ABCD) | Phase A Current
40076..40077 | Amps PhaseB | FLOAT (byteorder: ABCD) | Phase B Current
40078..40079 | Amps PhaseC | FLOAT (byteorder: ABCD) | Phase C Current
40080..40081 | Phase Voltage AB | FLOAT (byteorder: ABCD) | Phase Voltage AB
40082..40083 | Phase Voltage BC | FLOAT (byteorder: ABCD) | Phase Voltage BC
40084..40085 | Phase Voltage CA | FLOAT (byteorder: ABCD) | Phase Voltage CA
40086..40087 | Phase Voltage AN | FLOAT (byteorder: ABCD) | Phase Voltage AN
40088..40089 | Phase Voltage BN | FLOAT (byteorder: ABCD) | Phase Voltage BN
40090..40091 | Phase Voltage CN | FLOAT (byteorder: ABCD) | Phase Voltage CN
40092..40093 | Watts | FLOAT (byteorder: ABCD) | AC Power | x
40094..40095 | Hz | FLOAT (byteorder: ABCD) | Line Frequency
40096..40097 | VA | FLOAT (byteorder: ABCD) | AC Apparent Power | x
40098..40099 | VAr | FLOAT (byteorder: ABCD) | AC Reactive Power | x
40100..4010 | PF | FLOAT (byteorder: ABCD) | AC Power Factor | x
40102..40103 | WattHours | FLOAT (byteorder: ABCD) | AC Energy | x
40104..40105 | DC Amps | FLOAT (byteorder: ABCD) | DC Current
40106..40107 | DC Voltage | FLOAT (byteorder: ABCD) | DC Voltage
40108..40109 | DC Watts | FLOAT (byteorder: ABCD) | DC Power
40110..40111 | Cabinet Temperature | FLOAT (byteorder: ABCD) | Cabinet Temperature
40112..40113 | Heat Sink Temperature | FLOAT (byteorder: ABCD) | Heat Sink Temperature
40114..40115 | Transformer Temperature | FLOAT (byteorder: ABCD) | Transformer Temperature
40116..40117 | Other Temperature | FLOAT (byteorder: ABCD) | Other Temperature
40118 | Operating State | enum16 | Enumerated value. Operating state
40119 | Vendor Operating State | enum16 | Vendor specific operating state code
40120..40121 | Event1 | bitfield32 | Bitmask value. Event fields
40122..40123 | Event Bitfield 2 | bitfield32 | Reserved for future use
40124..40125 | Vendor Event Bitfield 1 | bitfield32 | Vendor defined events
40126..40127 | Vendor Event Bitfield 2 | bitfield32 | Vendor defined events
40128..40129 | Vendor Event Bitfield 3 | bitfield32 | Vendor defined events
40130..40131 | Vendor Event Bitfield 4 | bitfield32 | Vendor defined events
40132 | ID | 16 unsigned int | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | x
40133 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 30 | x
40134 | WMax | 16 unsigned int | Setting for maximum power output. Default to WRtg. | x
40135 | VRef | 16 unsigned int | Voltage at the PCC.
40136 | VRefOfs | 16 signed int | Offset from PCC to inverter.
40137 | VMax | 16 unsigned int | Setpoint for maximum voltage.
40138 | VMin | 16 unsigned int | Setpoint for minimum voltage.
40139 | VAMax | 16 unsigned int | Setpoint for maximum apparent power. Default to VARtg. | x
40140 | VArMaxQ1 | 16 signed int | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | x
40141 | VArMaxQ2 | 16 signed int | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | x
40142 | VArMaxQ3 | 16 signed int | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | x
40143 | VArMaxQ4 | 16 signed int | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | x
40144 | WGra | 16 unsigned int | Default ramp rate of change of active power due to command or internal action.
40145 | PFMinQ1 | 16 signed int | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1.
40146 | PFMinQ2 | 16 signed int | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2.
40147 | PFMinQ3 | 16 signed int | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3.
40148 | PFMinQ4 | 16 signed int | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4.
40149 | VArAct | enum16 | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
40150 | ClcTotVA | enum16 | Calculation method for total apparent power. 1=vector 2=arithmetic.
40151 | MaxRmpRte | 16 unsigned int | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
40152 | ECPNomHz | 16 unsigned int | Setpoint for nominal frequency at the ECP.
40153 | ConnPh | enum16 | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
40154 | WMax_SF | sunssf | Scale factor for real power. | x
40155 | VRef_SF | sunssf | Scale factor for voltage at the PCC.
40156 | VRefOfs_SF | sunssf | Scale factor for offset voltage.
40157 | VMinMax_SF | sunssf | Scale factor for min/max voltages.
40158 | VAMax_SF | sunssf | Scale factor for apparent power. | x
40159 | VArMax_SF | sunssf | Scale factor for reactive power. | x
40160 | WGra_SF | sunssf | Scale factor for default ramp rate.
40161 | PFMin_SF | sunssf | Scale factor for minimum power factor.
40162 | MaxRmpRte_SF | sunssf | Scale factor for maximum ramp percentage.
40163 | ECPNomHz_SF | sunssf | Scale factor for nominal frequency.
40164 | ID | 16 unsigned int | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | x
40165 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 24 | x
40166 | Conn_WinTms | 16 unsigned int | Time window for connect/disconnect.
40167 | Conn_RvrtTms | 16 unsigned int | Timeout period for connect/disconnect.
40168 | Conn | enum16 | Enumerated valued. Connection control.
40169 | WMaxLimPct | 16 unsigned int | Set power output to specified level. | x
40170 | WMaxLimPct_WinTms | 16 unsigned int | Time window for power limit change.
40171 | WMaxLimPct_RvrtTms | 16 unsigned int | Timeout period for power limit.
40172 | WMaxLimPct_RmpTms | 16 unsigned int | Ramp time for moving from current setpoint to new setpoint.
40173 | WMaxLim_Ena | enum16 | Enumerated valued. Throttle enable/disable control. | x
40174 | OutPFSet | 16 signed int | Set power factor to specific value - cosine of angle.
40175 | OutPFSet_WinTms | 16 unsigned int | Time window for power factor change.
40176 | OutPFSet_RvrtTms | 16 unsigned int | Timeout period for power factor.
40177 | OutPFSet_RmpTms | 16 unsigned int | Ramp time for moving from current setpoint to new setpoint.
40178 | OutPFSet_Ena | enum16 | Enumerated valued. Fixed power factor enable/disable control.
40179 | VArWMaxPct | 16 signed int | Reactive power in percent of WMax.
40180 | VArMaxPct | 16 signed int | Reactive power in percent of VArMax. | x
40181 | VArAvalPct | 16 signed int | Reactive power in percent of VArAval.
40182 | VArPct_WinTms | 16 unsigned int | Time window for VAR limit change.
40183 | VArPct_RvrtTms | 16 unsigned int | Timeout period for VAR limit.
40184 | VArPct_RmpTms | 16 unsigned int | Ramp time for moving from current setpoint to new setpoint.
40185 | VArPct_Mod | enum16 | Enumerated value. VAR percent limit mode. | x (2)
40186 | VArPct_Ena | enum16 | Enumerated valued. Percent limit VAr enable/disable control. | x
40187 | WMaxLimPct_SF | sunssf | Scale factor for power output percent. | x (-2)
40188 | OutPFSet_SF | sunssf | Scale factor for power factor.
40189 | VArPct_SF | sunssf | Scale factor for reactive power percent. | x (-2)
40190 | ID | 16 unsigned int | A well-known value 0xFFFF. Uniquely identifies this as a SunSpec End Model | x

## Coils 0x01
Proprietary profile
Address | DataLabel | DataType | Description | Note
Page05 (DNP3 control) |  |  |  | Page05 needs to be enabled
4000 | PV Ctrl. Active | Boolean | Superior power control from DNP3 (page05) active
4001 | PV Ramp Ctrl. Active | Boolean | Superior power ramp control from DNP3 (page05) active
4002..4999 | Reserved