## Meter data
Data label / Protocol | Pilot SPM32 | Pilot SPM33 | Acuvim-L | Acuvim EV300 | Schneider iEM3000 | Schneider PM51XX | Schneider PM53XX | Schneider PM55XX | Deif ml2 | Deif CGC400 | Cummins PC2.x | Cummins PC3.x | Cat EMCP4 | DSE GenComm | Deif ml2 Mains | Entes EPM07S | Janitza UMG96RM | Comap AMF20/25 | Comap InteliLite9 | Comap InteliGen | Comap InteliSys | Schneider PM1200/EM64XX | DEIF MIC-2 | Comap InteliComact | WW EasyGen2000 | WW EasyGen3000 | Klemsan Ercas | Klemsan Krea | Klemsan Powys | Phoenix EEM-EM3XX | Pheonix EMPro | Eastron SDM630 | Schneider PM2XXX | SmartGen HGM400 | Socomec Diris A40 | Chint DTSU/DSSU 666 | Lovato SGK60 | Secure Elite 440 | ABB M4M 30 | Secure Elite 300 | Aldogue UPM209 | PILOT PMAC770 | SmartGen HGM 7X00_9X00 | Circutor CVM C4 | Sices GC310/350/500 | Sices MC100 | Huawei Smartlogger | Elgris Smartmeter | CG EM/ET 300 series | WW EasyGen3000XT | LETTEL MCT4 | SIEMENS PCS3120 | AcuvimII | SGC120/121 | DFUN DFPM93 | LETTEL MCX-34V | Datakom D300_500_700 | Comap InteliGen_4_200 | Comap InteliMains_210 | Acrel ADL3000-E | Selec MFM384 | SMA DataManager | Sices MC200_400 | Cummins MCM3320 | Siemens 7kt0310 | IME Nemo96EA | Comap InteliGen 1000 | WEG MMW03 | Meier CMM62 | DM1000 | Meatrol ME337 | Legrand EMDX3 | Meier CMM62
AC power phase L1 | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x
AC power phase L2 | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x
AC power phase L3 | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x
AC power total | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC reactive power phase L1 | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x
AC reactive power phase L2 | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x
AC reactive power phase L3 | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | % | x | x | x | x | x
AC reactive power total | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC apparent power phase L1 | % | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | % | x | x | x | x
AC apparent power phase L2 | % | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | % | x | x | x | x
AC apparent power phase L3 | % | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | x | % | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | % | % | x | x | x | x
AC apparent power total | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | x | x
AC power factor phase L1 | x | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | % | x | x | x | % | x | x | x | x | x
AC power factor phase L2 | x | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | % | x | x | x | % | x | x | x | x | x
AC power factor phase L3 | x | x | x | % | % | % | % | % | % | % | % | % | x | x | % | x | x | x | x | x | x | % | x | x | % | % | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | % | x | x | % | x | % | x | x | x | % | x | x | x | x | x
AC power factor total | x | x | x | x | % | % | % | % | x | x | x | x | x | x | x | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
AC current phase L1 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | % | x | x | x | x | x | % | x | x | x | x | x
AC current phase L2 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | % | x | x | x | x | x | % | x | x | x | x | x
AC current phase L3 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | % | x | % | x | x | x | x | x | % | x | x | x | x | x
AC current neutral conducter | x | x | x | x | x | x | x | x | % | % | x | x | % | % | % | x | x | % | % | % | % | % | x | % | % | % | x | x | x | x | x | % | x | % | x | % | % | x | x | x | x | x | % | % | x | x | % | % | % | % | % | % | x | % | % | % | x | % | % | % | % | % | x | % | % | x | % | % | % | % | x | x | x
AC voltage L1-neutral | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x
AC voltage L2-neutral | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x
AC voltage L3-neutral | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | % | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x
AC voltage L1-L2 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x
AC voltage L2-L3 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x
AC voltage L3-L1 | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | x | x | x | x | x | x
AC frequency phase L1 | x | x | x | x | % | % | % | % | x | x | % | % | % | % | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | % | x | x | x | % | % | x | % | x | x | x | x | x | x | % | x | x | % | x | x | x | x | x | x | x | x | x | % | x | x | x | x | x | x | x | % | x | x | % | x | x
AC frequency phase L2 | % | % | % | % | % | % | % | % | x | x | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
AC frequency phase L3 | % | % | % | % | % | % | % | % | x | x | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
AC energy total | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | x | % | % | % | % | x | x | x | % | % | % | x | % | % | % | x | % | % | % | % | % | % | % | %
AC energy imported total | x | x | x | % | x | % | % | % | % | % | % | % | % | x | % | % | x | % | % | % | % | x | x | % | % | % | % | % | % | x | x | % | x | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | % | % | % | % | % | % | x | % | x | x | % | % | x | x | x | x | x
AC energy exported total | x | x | x | % | x | % | % | % | % | % | % | % | % | x | % | % | x | % | % | % | % | x | x | % | % | % | % | % | % | x | x | % | x | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | % | % | % | % | % | % | x | % | x | x | % | % | x | x | x | x | x
AC reactive energy total | x | x | % | % | % | % | % | % | % | % | % | % | % | x | % | % | x | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | x | % | % | % | % | x | x | % | % | % | % | x | % | % | % | x | % | % | % | % | % | % | % | %
AC reactive inductive energy total | x | x | x | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | x | % | % | % | % | % | % | % | x | % | x | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | x | % | % | % | % | % | x | % | x | x | % | % | x | x | x | x | x
AC reactive capacitive energy total | x | x | x | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | x | % | % | % | % | % | % | % | x | % | x | % | % | % | % | % | % | % | x | x | % | x | % | x | x | x | x | % | x | % | % | x | x | x | x | % | % | % | % | % | x | % | x | x | % | % | x | x | x | x | x
Digital input | x | x | % | x | x | x | x | x | x | x | x | x | x | % | x | x | % | x | x | x | x | % | x | x | x | x | % | % | % | x | x | % | % | % | % | % | % | % | % | % | % | x | % | x | % | % | % | % | % | x | % | % | % | x | % | % | % | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | %
Digital output | x | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | x | % | % | % | % | % | % | % | % | % | % | x | % | x | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
DG Management start/stop command | Relay | Relay | % | % | % | % | % | % | communication | communication | % | % | % | % | % | % | Relay | % | % | % | % | % | Relay | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | Relay | % | Relay | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %

## Meters info
GENERAL INFORMATION
The ECgrid will be reading various data from genset controllers and/or power meters. The data is presented on the ECweb as well as made availbale via Modbus. Some of the data are possible to push to cloud as well. A gross list of which data the ECgrid is able to read out is shown below along with indications of which data from the gross list are read from the protocols supported. Digital input can be used for breaker closed feedback.
SPECIFIC INFORMATION
JanitzaUMG96 protocol: Outouts need to be configured to Modbus control. Initial setup of outouts required in accordance with Janitza documentation
Schneider: Float byte order in the metres must set to Big-Endian.

## IO data
Data label / Protocol | EX0008DD | EX1600DD | EX16008DD | Huawei Smartlogger | DEIF ML2 BTB | DSE8680 | EX04AIO | EX04AIS | Woodward LS-5
Digital input | 0 | 16 | 16 | 8 | 1 | 1 | 0 | 0 | 8
Digital output | 8 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Analogue Input | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0
Analogue output | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0

## IO info
GENERAL INFORMATION
The ECpv is capable of interfacing to IO modules. Up to 4 IO modules can be connected. The data is presented on the ECweb as well as made available via Modbus.
SPECIFIC INFORMATION
DEIF ML2 BTB: The input read is the position of the busbar coupler
DSE8680: The input read is the position of the busbar coupler
EX04AIO/EX04AIS: The input and output can be selected as 0-10V or 0-20mA.
Woodward LS-5: The inputs read are the 8 discrete inputs on the device